## HELAT AL NAHADAH
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Ibri | HELAT AL NAHADAH | K_LN2 | 23.170301, 56.45696 | 1589 | Pole (PMT) | 3 | 315 | 05/06/2026, 15:13 | 1 | 234 | 235 | 236 | 403 | 408 | 408 | 120 mm² |  | 83 | 52 | 78 | 26 | 185 mm² |  | 61 | 57 | 66 | 6 | [32 empty] | Total Load R: 144; Total Load Y: 109; Total Load B: 144; Total Load N: 32 | 144 | 109 | 31.9093 | OK - No Upgrade | OK - Balanced
Ibri | HELAT AL NAHADAH | K_LN2 | 23.172512, 56.462625 | 1331 | Pole (PMT) | 3 | 315 | 05/06/2026, 15:08 | 1 | 235 | 236 | 221 | 406 | 402 | 409 | 185 mm² |  | 52 | 30 | 18 | 25 | 120 mm² |  | 11 | 12 | 4 | 8 | [32 empty] | Total Load R: 63; Total Load Y: 42; Total Load B: 22; Total Load N: 33 | 63 | 22 | 14.0643 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN2 | 23.169324, 56.471644 | 1697 | Pole (PMT) | 3 | 315 | 05/06/2026, 15:01 | 1 | 235 | 235 | 237 | 405 | 410 | 410 | 185 mm² |  | 31 | 1 | 23 | 26 | 185 mm² |  | 13 | 1 | 1 | 11 | 185 mm² |  | 0 | 0 | 0 | 0 | [26 empty] | Total Load R: 44; Total Load Y: 2; Total Load B: 24; Total Load N: 37 | 44 | 2 | 9.7985 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN2 | 23.168744, 56.470718 | 1567 | Ground (GMT) | 3 | 1000 | 05/06/2026, 14:52 | 1 | 235 | 236 | 238 | 406 | 410 | 412 | 185 mm² |  | 35 | 25 | 38 | 23 | 185 mm² |  | 32 | 0 | 0 | 27 | 120 mm² |  | 0 | 1 | 0 | 0 | 120 mm² |  | 0 | 18 | 18 | 13 | 185 mm² |  | 0 | 0 | 0 | 0 | [14 empty] | Total Load R: 67; Total Load Y: 44; Total Load B: 56; Total Load N: 63 | 67 | 44 | 4.7115 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN2 | 23.168218, 56.470623 | 176 | Ground (GMT) | 3 | 500 | 05/06/2026, 14:43 | 1 | 235 | 236 | 238 | 407 | 411 | 411 | 120 mm² |  | 9 | 0 | 8 | 0 | 185 mm² |  | 0 | 0 | 0 | 2 | 120 mm² |  | 0 | 0 | 0 | 0 | [26 empty] | Total Load R: 9; Total Load Y: 0; Total Load B: 8; Total Load N: 2 | 9 | 0 | 1.2689 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN2 | 23.172043, 56.469507 | 2165 | Ground (GMT) | 3 | 1000 | 05/06/2026, 14:35 | 1 | 235 | 235 | 238 | 406 | 412 | 411 | [30 empty] | 185 mm² |  | 46 | 0 | 9 | 8 | 185 mm² |  | 3 | 40 | 5 | 15 | 185 mm² |  | 13 | 0 | 0 | 11 | 62 | 40 | 14 | 34 | 62 | 14 | 4.3599 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN2 | 23.176973, 56.475117 | 1546 | Pole (PMT) | 3 | 315 | 05/06/2026, 14:27 | 1 | 233 | 234 | 237 | 402 | 411 | 407 | 185 mm² |  | 88 | 46 | 67 | 32 | 185 mm² |  | 97 | 68 | 25 | 63 | [32 empty] | Total Load R: 185; Total Load Y: 114; Total Load B: 92; Total Load N: 95 | 185 | 92 | 40.8929 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN2 | 23.172978, 56.469913 | 1857 | Ground (GMT) | 3 | 1000 | 05/06/2026, 14:21 | 1 | 236 | 236 | 239 | 406 | 412 | 412 | 185 mm² |  | 50 | 19 | 16 | 30 | 185 mm² |  | 59 | 52 | 46 | 37 | 240 mm² |  | 0 | 1 | 20 | 16 | 185 mm² |  | 41 | 52 | 67 | 21 | 185 mm² |  | 30 | 28 | 37 | 11 | [14 empty] | Total Load R: 180; Total Load Y: 152; Total Load B: 186; Total Load N: 115 | 186 | 152 | 13.0798 | OK - No Upgrade | OK - Balanced
Ibri | HELAT AL NAHADAH | K_LN2 | 23.177215, 56.469691 | 2094 | Ground (GMT) | 3 | 1000 | 05/06/2026, 14:12 | 1 | 236 | 236 | 239 | 408 | 412 | 413 | [36 empty] | 185 mm² |  | 43 | 39 | 34 | 10 | 185 mm² |  | 17 | 16 | 0 | 8 | 60 | 55 | 34 | 18 | 60 | 34 | 4.2401 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN2 | 23.176804, 56.468373 | 1848 | Pole (PMT) | 3 | 315 | 05/06/2026, 14:07 | 1 | 237 | 236 | 239 | 408 | 413 | 412 | 185 mm² |  | 14 | 34 | 60 | 32 | 185 mm² |  | 27 | 22 | 6 | 20 | [32 empty] | Total Load R: 41; Total Load Y: 56; Total Load B: 66; Total Load N: 52 | 66 | 41 | 14.8066 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN2 | 23.185852, 56.480448 | 172 | Ground (GMT) | 3 | 1000 | 04/06/2026, 15:40 | 1 | 233 | 233 | 235 | 402 | 408 | 407 | [24 empty] | 185 mm² |  | 36 | 60 | 55 | 15 | 185 mm² |  | 120 | 86 | 90 | 44 | 185 mm² |  | 20 | 0 | 0 | 21 |  |  | Total Load R: 176; Total Load Y: 146; Total Load B: 145; Total Load N: 80 | 176 | 145 | 12.2546 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN2 | 23.188089, 56.480729 | 169 | Ground (GMT) | 3 | 1000 | 04/06/2026, 15:30 | 1 | 232 | 232 | 235 | 402 | 406 | 404 |  |  | 154 | 113 | 134 | [7 empty] | 185 mm² |  | 141 | 114 | 155 | 0 | 185 mm² |  | 155 | 105 | 151 | 28 | 240 mm² |  | 36 | 41 | 12 | 16 | [14 empty] | Total Load R: 486; Total Load Y: 373; Total Load B: 452; Total Load N: 44 | 486 | 373 | 33.8394 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN2 | 23.18584, 56.473754 | 1692 | Pole (PMT) | 3 | 315 | 04/06/2026, 15:05 | 1 | 233 | 233 | 235 | 402 | 406 | 406 | 185 mm² |  | 33 | 64 | 41 | 17 | 185 mm² |  | 70 | 73 | 82 | 13 | [32 empty] | Total Load R: 103; Total Load Y: 137; Total Load B: 123; Total Load N: 30 | 137 | 103 | 30.2828 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN2 | 23.187853, 56.475304 | 1443 | Ground (GMT) | 3 | 1000 | 04/06/2026, 14:59 | 1 | 233 | 234 | 236 | 404 | 408 | 407 | 185 mm² |  | 51 | 38 | 25 | 22 | 185 mm² |  | 48 | 36 | 9 | 19 | 185 mm² |  | 41 | 27 | 32 | 8 | 185 mm² |  | 40 | 49 | 34 | 10 | [20 empty] | Total Load R: 180; Total Load Y: 150; Total Load B: 100; Total Load N: 59 | 180 | 100 | 12.5955 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN2 | 23.188559, 56.476453 | 1776 | Ground (GMT) | 3 | 1000 | 04/06/2026, 14:54 | 1 | 234 | 235 | 237 | 404 | 408 | 408 | 300 mm² |  | 61 | 26 | 40 | 81 |  |  | 77 | 25 | 49 | 78 | [32 empty] | Total Load R: 138; Total Load Y: 51; Total Load B: 89; Total Load N: 159 | 138 | 51 | 9.6565 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN13 | 23.212206, 56.501779 | 1657 | Pole (PMT) |  | 315 | 31/05/2026, 15:23 | 1 | 244 | 242 | 245 | 421 | 424 | 422 | 120 mm² |  | 30 | 40 | 26 | 13 | 120 mm² |  | 18 | 33 | 25 | 18 | [32 empty] | Total Load R: 48; Total Load Y: 73; Total Load B: 51; Total Load N: 31 | 73 | 48 | 16.8988 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN13 | 23.203594, 56.513526 | 1636 | Ground (GMT) |  | 1000 | 31/05/2026, 15:15 | 1 | 231 | 230 | 232 | 396 | 402 | 401 | 185 mm² |  | 12 | 55 | 36 | 37 | 185 mm² |  | 24 | 40 | 30 | 9 | 185 mm² |  | 41 | 47 | 23 | 24 | 185 mm² |  | 95 | 75 | 22 | 29 | [20 empty] | Total Load R: 172; Total Load Y: 217; Total Load B: 111; Total Load N: 99 | 217 | 111 | 14.8839 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN13 | 23.20023, 56.516996 | 323 | Pole (PMT) |  | 315 | 31/05/2026, 15:05 | 1 | 240 | 237 | 233 | 413 | 417 | 412 | 185 mm² |  | 90 | 189 | 126 | 59 | 185 mm² |  | 171 | 132 | 140 | 34 | [32 empty] | Total Load R: 261; Total Load Y: 321; Total Load B: 266; Total Load N: 93 | 321 | 261 | 72.8962 | Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN13 | 23.1984, 56.515401 | 324 | Pole (PMT) |  | 315 | 31/05/2026, 15:00 | 1 | 239 | 240 | 242 | 413 | 419 | 418 | 185 mm² |  | 151 | 49 | 112 | 29 | 185 mm² |  | 84 | 42 | 9 | 50 | 185 mm² |  | 0 | 0 | 0 | 0 | [26 empty] | Total Load R: 235; Total Load Y: 91; Total Load B: 121; Total Load N: 79 | 235 | 91 | 53.3664 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN13 | 23.194525, 56.51296 | 325 | Pole (PMT) |  | 315 | 31/05/2026, 14:52 | 1 | 241 | 241 | 242 | 416 | 418 | 420 | 185 mm² |  | 52 | 40 | 97 | 47 | 185 mm² |  | 70 | 49 | 70 | 16 | [32 empty] | Total Load R: 122; Total Load Y: 89; Total Load B: 167; Total Load N: 63 | 167 | 89 | 38.1997 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN13 | 23.190727, 56.5097 | 2194 | Ground (GMT) |  | 1000 | 31/05/2026, 14:44 | 1 | 241 | 240 | 244 | 416 | 422 | 421 | [24 empty] | 185 mm² |  | 88 | 45 | 34 | 37 | 185 mm² |  | 70 | 148 | 108 | 70 | [8 empty] | Total Load R: 158; Total Load Y: 193; Total Load B: 142; Total Load N: 107 | 193 | 142 | 13.9063 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN13 | 23.185605, 56.503077 | 4319 | Pole (PMT) |  | 100 | 31/05/2026, 14:37 | 1 | 242 | 240 | 244 | 419 | 421 | 420 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | HELAT AL NAHADAH | K_LN13 | 23.193496, 56.507437 | 2195 | Pole (PMT) |  | 315 | 31/05/2026, 14:33 | 1 | 242 | 241 | 243 | 418 | 421 | 420 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 12 | 11 | [32 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 12; Total Load N: 11 | 12 | 0 | 2.7581 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN13 | 23.197447, 56.50931 | 326 | Pole (PMT) |  | 315 | 31/05/2026, 14:28 | 1 | 239 | 236 | 240 | 410 | 416 | 412 | 120 mm² |  | 91 | 81 | 97 | 18 | 120 mm² |  | 11 | 62 | 32 | 39 | [32 empty] | Total Load R: 102; Total Load Y: 143; Total Load B: 129; Total Load N: 57 | 143 | 102 | 32.2381 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN13 | 23.199939, 56.506808 | 327 | Pole (PMT) |  | 315 | 31/05/2026, 14:24 | 1 | 242 | 241 | 245 | 418 | 424 | 420 | 120 mm² |  | 3 | 20 | 2 | 17 | 120 mm² |  | 16 | 15 | 11 | 15 | [32 empty] | Total Load R: 19; Total Load Y: 35; Total Load B: 13; Total Load N: 32 | 35 | 13 | 8.0444 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN3 |  | 4398 | Ground (GMT) |  | 1000 | 31/05/2026, 14:23 | 1 | 242 | 243 | 245 | 422 | 427 | 430 | [24 empty] | 240 mm² |  | 0 | 0 | 0 | 0 | 240 mm² |  | 35 | 56 | 124 | 77 | 240 mm² |  | 48 | 78 | 74 | 26 | 240 mm² |  | 43 | 122 | 56 | 71 | 126 | 256 | 254 | 174 | 256 | 126 | 18.7117 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN13 | 23.202085, 56.510048 | 2193 | Ground (GMT) |  | 1000 | 31/05/2026, 14:19 | 1 | 240 | 239 | 242 | 414 | 419 | 416 | 185 mm² |  | 12 | 28 | 16 | 10 | 185 mm² |  | 92 | 101 | 55 | 20 | [32 empty] | Total Load R: 104; Total Load Y: 129; Total Load B: 71; Total Load N: 30 | 129 | 71 | 9.2502 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN3 |  | 4626 | Ground (GMT) |  | 500 | 31/05/2026, 14:16 | 1 | 243 | 243 | 246 | 420 | 426 | 425 | 70 mm² |  | 0 | 12 | 0 | 12 | 70 mm² |  | 25 | 2 | 0 | 26 | 70 mm² |  | 8 | 0 | 0 | 8 | [26 empty] | Total Load R: 33; Total Load Y: 14; Total Load B: 0; Total Load N: 46 | 33 | 0 | 4.8012 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN13 | 23.205274, 56.510729 | 302 | Pole (PMT) |  | 315 | 31/05/2026, 14:11 | 1 | 237 | 239 | 240 | 409 | 414 | 415 | 120 mm² |  | 218 | 103 | 132 | 88 | 120 mm² |  | 97 | 98 | 147 | 30 | [32 empty] | Total Load R: 315; Total Load Y: 201; Total Load B: 279; Total Load N: 118 | 315 | 201 | 70.8409 | Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN3 |  | 1737 | Ground (GMT) |  | 1000 | 31/05/2026, 14:07 | 1 | 243 | 242 | 245 | 419 | 426 | 423 | [12 empty] | 185 mm² |  | 135 | 123 | 90 | 51 | [6 empty] | 185 mm² |  | 62 | 88 | 83 | 19 | 185 mm² |  | 120 | 134 | 146 | 26 | [8 empty] | Total Load R: 317; Total Load Y: 345; Total Load B: 319; Total Load N: 96 | 345 | 317 | 25.0377 | OK - No Upgrade | OK - Balanced
Ibri | HELAT AL NAHADAH | K_LN13 | 23.207187, 56.506485 | 303 | Pole (PMT) |  | 100 | 31/05/2026, 14:01 | 1 | 237 | 237 | 240 | 410 | 413 | 413 |  |  | 57 | 58 | 61 | 5 | [38 empty] | Total Load R: 57; Total Load Y: 58; Total Load B: 61; Total Load N: 5 | 61 | 57 | 43.3186 | OK - No Upgrade | OK - Balanced
Ibri | HELAT AL NAHADAH | K_LN3 |  | 163 | Ground (GMT) |  | 1000 | 31/05/2026, 14:00 | 1 | 244 | 243 | 247 | 420 | 427 | 426 | 185 mm² |  | 68 | 33 | 28 | 32 | 185 mm² |  | 76 | 88 | 45 | 28 | 185 mm² |  | 32 | 103 | 66 | 57 | 185 mm² |  | 52 | 11 | 3 | 38 | [20 empty] | Total Load R: 228; Total Load Y: 235; Total Load B: 142; Total Load N: 155 | 235 | 142 | 17.0953 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN13 | 23.214745, 56.506732 | 301 | Ground (GMT) |  | 500 | 31/05/2026, 13:54 | 1 | 240 | 241 | 244 | 413 | 422 | 420 | [12 empty] | 240 mm² |  | 95 | 60 | 106 | 50 | 185 mm² |  | 70 | 25 | 13 | 52 | 185 mm² |  | 157 | 70 | 65 | 78 | [14 empty] | Total Load R: 322; Total Load Y: 155; Total Load B: 184; Total Load N: 180 | 322 | 155 | 46.0677 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN3 |  | 297 | Ground (GMT) |  | 1000 | 31/05/2026, 13:52 | 1 | 243 | 243 | 246 | 422 | 425 | 426 | [12 empty] | 185 mm² |  | 144 | 98 | 99 | 46 | 185 mm² |  | 111 | 164 | 126 | 32 | 185 mm² |  | 60 | 84 | 90 | 37 | 185 mm² |  | 54 | 69 | 53 | 39 | [8 empty] | Total Load R: 369; Total Load Y: 415; Total Load B: 368; Total Load N: 154 | 415 | 368 | 30.3334 | OK - No Upgrade | OK - Balanced
Ibri | HELAT AL NAHADAH | K_LN13 | 23.214171, 56.506727 | 4405 | Ground (GMT) |  | 1000 | 31/05/2026, 13:46 | 1 | 243 | 242 | 246 | 419 | 426 | 424 | [36 empty] | 185 mm² |  | 0 | 18 | 17 | 15 | 185 mm² |  | 120 | 42 | 56 | 38 | 120 | 60 | 73 | 53 | 120 | 60 | 8.7088 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN3 |  | 142 | Ground (GMT) |  | 1000 | 31/05/2026, 13:44 | 1 | 240 | 242 | 246 | 420 | 425 | 424 | [12 empty] | 185 mm² |  | 51 | 40 | 81 | 33 | 120 mm² |  | 7 | 17 | 6 | 10 | 185 mm² |  | 68 | 119 | 67 | 52 | [14 empty] | Total Load R: 126; Total Load Y: 176; Total Load B: 154; Total Load N: 95 | 176 | 126 | 12.8033 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN13 | 23.216146, 56.503513 | 4647 | Ground (GMT) |  | 1000 | 31/05/2026, 13:38 | 1 | 237 | 236 | 239 | 408 | 413 | 411 | [44 empty] | 28 | 25 | 20 | 8 | 28 | 25 | 20 | 8 | 28 | 20 | 1.9787 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN3 |  | 144 | Ground (GMT) |  | 1000 | 31/05/2026, 13:32 | 1 | 246 | 243 | 244 | 426 | 428 | 421 | 185 mm² |  | 112 | 139 | 120 | 27 | 185 mm² |  | 109 | 46 | 138 | 80 | 185 mm² |  | 0 | 0 | 0 | 0 | [6 empty] | 185 mm² |  | 55 | 23 | 70 | 54 | 240 mm² |  | 0 | 0 | 0 | 0 | [8 empty] | Total Load R: 276; Total Load Y: 208; Total Load B: 328; Total Load N: 161 | 328 | 208 | 24.2016 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 159 | Ground (GMT) |  | 1000 | 30/05/2026, 16:08 | 1 | 242 | 241 | 244 | 418 | 425 | 420 | 185 mm² |  | 66 | 0 | 40 | 27 | 185 mm² |  | 54 | 84 | 62 | 14 | 185 mm² |  | 64 | 62 | 101 | 36 | 185 mm² |  | 78 | 58 | 42 | 32 | 185 mm² |  | 119 | 125 | 75 | 46 | 185 mm² |  | 105 | 139 | 120 | 27 | [8 empty] | Total Load R: 486; Total Load Y: 468; Total Load B: 440; Total Load N: 182 | 486 | 440 | 35.1863 | OK - No Upgrade | OK - Balanced
Ibri | HELAT AL NAHADAH | K_LN15 |  | 1402 | Ground (GMT) |  | 500 | 30/05/2026, 15:53 | 1 | 241 | 241 | 244 | 414 | 424 | 420 | 185 mm² |  | 119 | 75 | 57 | 62 | 185 mm² |  | 84 | 59 | 36 | 12 | 185 mm² |  | 191 | 66 | 86 | 30 | 185 mm² |  | 22 | 18 | 22 | 11 | [20 empty] | Total Load R: 416; Total Load Y: 218; Total Load B: 201; Total Load N: 115 | 416 | 201 | 59.6601 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 147 | Ground (GMT) |  | 1000 | 30/05/2026, 15:39 | 1 | 239 | 241 | 242 | 415 | 417 | 422 | [6 empty] | 120 mm² |  | 60 | 84 | 102 | 34 | 120 mm² |  | 135 | 147 | 54 | 81 | 120 mm² |  | 82 | 58 | 36 | 34 | 185 mm² |  | 116 | 183 | 142 | 43 | 185 mm² |  | 124 | 140 | 105 | 60 | 185 mm² |  | 106 | 89 | 99 | 18 |  |  | Total Load R: 623; Total Load Y: 701; Total Load B: 538; Total Load N: 270 | 701 | 538 | 50.388 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 158 | Ground (GMT) |  | 1000 | 30/05/2026, 15:18 | 1 | 234 | 233 | 230 | 403 | 409 | 407 | [18 empty] | 185 mm² |  | 34 | 55 | 46 | 17 | 185 mm² |  | 117 | 104 | 97 | 19 | 185 mm² |  | 81 | 131 | 116 | 15 | 185 mm² |  | 131 | 94 | 114 | 42 | 185 mm² |  | 243 | 92 | 150 | 148 | 606 | 476 | 523 | 241 | 606 | 476 | 42.2998 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 4372 | Ground (GMT) |  | 1000 | 30/05/2026, 14:58 | 1 | 243 | 242 | 245 | 420 | 425 | 424 | 185 mm² |  | 22 | 5 | 11 | 13 | [38 empty] | Total Load R: 22; Total Load Y: 5; Total Load B: 11; Total Load N: 13 | 22 | 5 | 1.6004 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 160 | Ground (GMT) |  | 1000 | 30/05/2026, 14:52 | 1 | 243 | 242 | 245 | 419 | 425 | 423 | [24 empty] | 185 mm² |  | 118 | 128 | 81 | 45 | 185 mm² |  | 18 | 69 | 22 | 31 | 120 mm² |  | 65 | 59 | 53 | 9 | 120 mm² |  | 56 | 37 | 44 | 15 | 257 | 293 | 200 | 100 | 293 | 200 | 21.2639 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 1306 | Ground (GMT) |  | 1000 | 30/05/2026, 14:41 | 1 | 242 | 242 | 246 | 420 | 426 | 424 | [12 empty] | 185 mm² |  | 6 | 19 | 38 | 29 | 185 mm² |  | 79 | 74 | 51 | 17 | [18 empty] | 185 mm² |  | 66 | 42 | 56 | 22 | 151 | 135 | 145 | 68 | 151 | 135 | 10.9847 | OK - No Upgrade | OK - Balanced
Ibri | HELAT AL NAHADAH | K_LN15 |  | 4707 | Ground (GMT) |  | 500 | 30/05/2026, 14:22 | 1 | 244 | 243 | 247 | 421 | 428 | 425 | 185 mm² |  | 34 | 24 | 30 | 5 | 185 mm² |  | 2 | 0 | 0 | 2 | [32 empty] | Total Load R: 36; Total Load Y: 24; Total Load B: 30; Total Load N: 7 | 36 | 24 | 5.2502 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 4515 | Pole (PMT) |  | 315 | 30/05/2026, 14:07 | 1 | 257 | 254 | 260 | 442 | 451 | 447 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 2 | 13 | 0 | 10 | [32 empty] | Total Load R: 2; Total Load Y: 13; Total Load B: 0; Total Load N: 10 | 13 | 0 | 3.1595 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 1946 | Ground (GMT) |  | 1000 | 30/05/2026, 14:00 | 1 | 243 | 242 | 245 | 418 | 426 | 423 | 185 mm² |  | 26 | 2 | 0 | 24 | 185 mm² |  | 5 | 13 | 0 | 11 | 185 mm² |  | 7 | 0 | 9 | 8 | 185 mm² |  | 11 | 10 | 10 | 3 | [20 empty] | Total Load R: 49; Total Load Y: 25; Total Load B: 19; Total Load N: 46 | 49 | 19 | 3.5476 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 1821 | Ground (GMT) |  | 1000 | 30/05/2026, 13:39 | 1 | 246 | 248 | 250 | 429 | 431 | 435 | 240 mm² |  | 21 | 17 | 11 | 8 | 240 mm² |  | 109 | 83 | 62 | 37 | 240 mm² |  | 79 | 46 | 44 | 21 | 240 mm² |  | 141 | 70 | 98 | 60 | [20 empty] | Total Load R: 350; Total Load Y: 216; Total Load B: 215; Total Load N: 126 | 350 | 215 | 26.0067 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 1188 | Ground (GMT) |  | 1000 | 29/05/2026, 15:28 | 1 | 242 | 242 | 247 | 423 | 428 | 427 | 185 mm² |  | 44 | 20 | 27 | 16 | 185 mm² |  | 15 | 12 | 0 | 14 | 185 mm² |  | 1 | 1 | 11 | 8 | [26 empty] | Total Load R: 60; Total Load Y: 33; Total Load B: 38; Total Load N: 38 | 60 | 33 | 4.3959 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 1720 | Ground (GMT) |  | 1000 | 29/05/2026, 15:22 | 1 | 243 | 242 | 246 | 419 | 425 | 424 | [12 empty] | 240 mm² |  | 3 | 3 | 0 | 3 | 185 mm² |  | 11 | 2 | 13 | 10 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 2 | 0 | 1 | 3 | 185 mm² |  | 28 | 15 | 0 | 18 | 185 mm² |  | 1 | 11 | 0 | 5 | 45 | 31 | 14 | 39 | 45 | 14 | 3.2658 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 1397 | Ground (GMT) |  | 1000 | 29/05/2026, 15:10 | 1 | 244 | 242 | 246 | 421 | 425 | 423 | 185 mm² |  | 48 | 43 | 32 | 11 | [38 empty] | Total Load R: 48; Total Load Y: 43; Total Load B: 32; Total Load N: 11 | 48 | 32 | 3.5001 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 1475 | Pole (PMT) |  | 315 | 29/05/2026, 15:04 | 1 | 240 | 242 | 245 | 421 | 425 | 422 | 185 mm² |  | 12 | 50 | 36 | 12 | 185 mm² |  | 30 | 11 | 26 | 23 | 185 mm² |  | 5 | 8 | 13 | 3 | [26 empty] | Total Load R: 47; Total Load Y: 69; Total Load B: 75; Total Load N: 38 | 75 | 47 | 17.3617 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 1752 | Ground (GMT) |  | 1000 | 29/05/2026, 14:54 | 1 | 243 | 242 | 245 | 418 | 424 | 423 | 185 mm² |  | 23 | 42 | 38 | 12 | 185 mm² |  | 71 | 31 | 46 | 43 | [32 empty] | Total Load R: 94; Total Load Y: 73; Total Load B: 84; Total Load N: 55 | 94 | 73 | 6.8056 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 1879 | Ground (GMT) |  | 1000 | 29/05/2026, 14:46 | 1 | 242 | 242 | 246 | 418 | 425 | 423 | 185 mm² |  | 16 | 11 | 48 | 31 | 185 mm² |  | 195 | 94 | 57 | 33 | 185 mm² |  | 150 | 89 | 49 | 40 | 185 mm² |  | 24 | 16 | 0 | 27 | 185 mm² |  | 0 | 7 | 21 | 11 | [14 empty] | Total Load R: 385; Total Load Y: 217; Total Load B: 175; Total Load N: 142 | 385 | 175 | 27.8739 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 1420 | Ground (GMT) |  | 1000 | 29/05/2026, 14:33 | 1 | 243 | 243 | 246 | 419 | 427 | 424 | [30 empty] | 185 mm² |  | 27 | 31 | 7 | 37 | 185 mm² |  | 23 | 45 | 34 | 12 | 185 mm² |  | 45 | 72 | 76 | 28 | 95 | 148 | 117 | 77 | 148 | 95 | 10.7408 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 162 | Ground (GMT) |  | 500 | 29/05/2026, 14:29 | 1 | 243 | 242 | 246 | 417 | 426 | 423 | 185 mm² |  | 118 | 55 | 91 | 64 | 185 mm² |  | 108 | 75 | 39 | 63 | [32 empty] | Total Load R: 226; Total Load Y: 130; Total Load B: 130; Total Load N: 127 | 226 | 130 | 32.6464 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 | 23.206667, 56.463081 | 1480 | Ground (GMT) |  | 500 | 29/05/2026, 14:18 | 1 | 242 | 242 | 245 | 416 | 424 | 423 | 185 mm² |  | 112 | 60 | 88 | 33 | 185 mm² |  | 19 | 2 | 22 | 15 | 185 mm² |  | 131 | 88 | 96 | 42 | 185 mm² |  | 26 | 24 | 43 | 15 | 185 mm² |  | 78 | 104 | 67 | 30 | [14 empty] | Total Load R: 366; Total Load Y: 278; Total Load B: 316; Total Load N: 135 | 366 | 278 | 52.743 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN15 |  | 1791 | Ground (GMT) |  | 1000 | 29/05/2026, 14:08 | 1 | 246 | 245 | 249 | 423 | 431 | 429 | [12 empty] | 185 mm² |  | 26 | 10 | 3 | 20 | 185 mm² |  | 28 | 21 | 10 | 9 | 120 mm² |  | 27 | 26 | 44 | 21 | 185 mm² |  | 11 | 23 | 9 | 15 | [6 empty] | 185 mm² |  | 5 | 8 | 5 | 3 | 97 | 88 | 71 | 68 | 97 | 71 | 7.1068 | OK - No Upgrade | Need to Balance
Ibri | HELAT AL NAHADAH | K_LN3 | 23.578, 58.4021 | 145 | Ground (GMT) |  | 500 | 03/05/2026, 07:59 | 1 | 243 | 243 | 251 | 430 | 434 | 433 | [12 empty] | 240 mm² |  | 55 | 46 | 46 | 15 | 185 mm² |  | 86 | 102 | 94 | 20 | 240 mm² |  | 170 | 169 | 219 | 51 | [14 empty] | Total Load R: 311; Total Load Y: 317; Total Load B: 359; Total Load N: 86 | 359 | 311 | 53.4753 | OK - No Upgrade | OK - Balanced

## SULAIF
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Ibri | SULAIF | K_LN2 | 23.212874, 56.511339 | 304 | Pole (PMT) | 3 | 315 | 13/06/2026, 15:02 | 1 | 245 | 247 | 247 | 431 | 430 | 430 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN2 | 23.215687, 56.5113 | 305 | Ground (GMT) | 3 | 1000 | 13/06/2026, 14:57 | 1 | 248 | 249 | 249 | 425 | 426 | 424 | [18 empty] | 120 mm² |  | 143 | 115 | 128 | 29 | 120 mm² |  | 88 | 42 | 61 | 52 | 185 mm² |  | 59 | 47 | 76 | 34 | 120 mm² |  | 24 | 46 | 33 | 15 | 120 mm² |  | 54 | 27 | 87 | 52 | 368 | 277 | 385 | 182 | 385 | 277 | 28.3407 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN2 | 23.214643, 56.513329 | 1554 | Ground (GMT) | 3 | 1000 | 13/06/2026, 14:47 | 1 | 245 | 248 | 247 | 425 | 424 | 425 | [12 empty] | 185 mm² |  | 144 | 150 | 120 | 37 | 185 mm² |  | 8 | 12 | 10 | 4 | 120 mm² |  | 31 | 28 | 18 | 35 | 185 mm² |  | 125 | 126 | 76 | 68 | 185 mm² |  | 54 | 83 | 51 | 33 | 185 mm² |  | 14 | 13 | 13 | 4 | 376 | 412 | 288 | 181 | 412 | 288 | 30.3282 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN2 | 23.214921, 56.514247 | 306 | Ground (GMT) | 3 | 1000 | 13/06/2026, 14:43 | 1 | 246 | 248 | 250 | 425 | 426 | 428 | [6 empty] | 185 mm² |  | 125 | 137 | 103 | 33 | 185 mm² |  | 3 | 16 | 6 | 7 | 120 mm² |  | 56 | 73 | 20 | 40 | 120 mm² |  | 40 | 49 | 24 | 19 | 120 mm² |  | 129 | 54 | 107 | 60 | 185 mm² |  | 129 | 108 | 59 | 56 | 185 mm² |  | 10 | 16 | 12 | 8 | 492 | 453 | 331 | 223 | 492 | 331 | 36.2172 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN2 |  | 322 | Ground (GMT) | 3 | 1000 | 13/06/2026, 14:28 | 1 | 247 | 249 | 249 | 433 | 437 | 435 | [6 empty] | 185 mm² |  | 22 | 42 | 37 | 73 | 120 mm² |  | 23 | 30 | 38 | 12 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 118 | 121 | 180 | 35 | 185 mm² |  | 26 | 7 | 66 | 44 | 185 mm² |  | 81 | 72 | 76 | 51 | 120 mm² |  | 146 | 192 | 134 | 51 | 416 | 464 | 531 | 266 | 531 | 416 | 39.8238 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN2 |  | 1378 | Pole (PMT) | 3 | 315 | 13/06/2026, 14:19 | 1 | 249 | 246 | 245 | 431 | 435 | 433 | 185 mm² |  | 91 | 55 | 61 | 34 | [38 empty] | Total Load R: 91; Total Load Y: 55; Total Load B: 61; Total Load N: 34 | 91 | 55 | 21.566 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN2 | 23.209377, 56.519107 | 1547 | Pole (PMT) | 3 | 200 | 13/06/2026, 14:14 | 1 | 244 | 243 | 248 | 426 | 424 | 426 | 185 mm² |  | 144 | 131 | 139 | 25 | [38 empty] | Total Load R: 144; Total Load Y: 131; Total Load B: 139; Total Load N: 25 | 144 | 131 | 53.1255 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN2 | 23.209205, 56.516966 | 318 | Ground (GMT) | 3 | 1000 | 13/06/2026, 14:08 | 1 | 250 | 251 | 254 | 433 | 435 | 440 | 185 mm² |  | 109 | 159 | 123 | 40 | [6 empty] | 185 mm² |  | 205 | 97 | 81 | 38 | 185 mm² |  | 27 | 0 | 6 | 47 | 185 mm² |  | 109 | 128 | 126 | 23 | 185 mm² |  | 58 | 58 | 29 | 32 | 185 mm² |  | 79 | 86 | 43 | 40 |  |  | Total Load R: 587; Total Load Y: 528; Total Load B: 408; Total Load N: 220 | 587 | 408 | 44.0237 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN2 | 23.212647, 56.519515 | 1522 | Ground (GMT) | 3 | 1000 | 13/06/2026, 13:58 | 1 | 246 | 245 | 250 | 425 | 432 | 433 | 185 mm² |  | 58 | 49 | 125 | 32 | 185 mm² |  | 85 | 61 | 86 | 43 | 185 mm² |  | 73 | 84 | 53 | 28 | 185 mm² |  | 47 | 46 | 31 | 22 | 185 mm² |  | 95 | 82 | 94 | 14 | 240 mm² |  | 43 | 29 | 155 | 100 | [8 empty] | Total Load R: 401; Total Load Y: 351; Total Load B: 544; Total Load N: 239 | 544 | 351 | 40.045 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN2 | 23.214666, 56.515388 | 310 | Ground (GMT) | 3 | 1000 | 13/06/2026, 13:48 | 1 | 245 | 245 | 248 | 423 | 429 | 430 | 185 mm² |  | 52 | 29 | 62 | 12 | [6 empty] | 120 mm² |  | 242 | 51 | 71 | 44 | 120 mm² |  | 24 | 87 | 74 | 67 | 120 mm² |  | 150 | 65 | 122 | 81 | 120 mm² |  | 0 | 51 | 27 | 26 | 120 mm² |  | 75 | 42 | 34 | 31 | 120 mm² |  | 10 | 50 | 56 | 46 | 553 | 375 | 446 | 307 | 553 | 375 | 40.516 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.199013, 56.488255 | 1947 | Pole (PMT) | 3 | 315 | 12/06/2026, 15:40 | 1 | 232 | 236 | 241 | 419 | 418 | 420 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 28 | 54 | 49 | 29 | [32 empty] | Total Load R: 28; Total Load Y: 54; Total Load B: 49; Total Load N: 29 | 54 | 28 | 12.4411 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.198808, 56.48834 | 458 | Pole (PMT) |  | 315 |  | 1 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN3 | 23.198272, 56.489639 | 2347 | Ground (GMT) | 3 | 1000 | 12/06/2026, 15:34 | 1 | 241 | 240 | 243 | 417 | 419 | 418 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 69 | 17 | 88 | 26 | 185 mm² |  | 19 | 36 | 3 | 24 | 185 mm² |  | 14 | 6 | 10 | 12 | [20 empty] | Total Load R: 102; Total Load Y: 59; Total Load B: 101; Total Load N: 62 | 102 | 59 | 7.3671 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN2 | 23.204466, 56.52293 | 321 | Ground (GMT) | 3 | 500 | 12/06/2026, 15:28 | 1 | 242 | 246 | 247 | 435 | 431 | 430 | [12 empty] | 185 mm² |  | 42 | 15 | 26 | 18 | 185 mm² |  | 82 | 98 | 112 | 30 | 185 mm² |  | 46 | 62 | 25 | 19 | 185 mm² |  | 92 | 160 | 102 | 49 | [8 empty] | Total Load R: 262; Total Load Y: 335; Total Load B: 265; Total Load N: 116 | 335 | 262 | 50.4806 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.192044, 56.486318 | 463 | Ground (GMT) | 3 | 1000 | 12/06/2026, 15:26 | 1 | 239 | 238 | 241 | 413 | 418 | 416 | 185 mm² |  | 96 | 74 | 78 | 14 | 185 mm² |  | 141 | 97 | 73 | 56 | 120 mm² |  | 58 | 44 | 55 | 22 | 185 mm² |  | 62 | 64 | 110 | 35 | 185 mm² |  | 2 | 0 | 0 | 2 | [12 empty] | 120 mm² |  | 80 | 65 | 62 | 22 | 439 | 344 | 378 | 151 | 439 | 344 | 31.4033 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN2 | 23.208287, 56.523188 | 320 | Ground (GMT) | 3 | 500 | 12/06/2026, 15:21 | 1 | 247 | 244 | 246 | 429 | 425 | 420 | [18 empty] | 185 mm² |  | 86 | 72 | 78 | 25 | 185 mm² |  | 120 | 91 | 131 | 36 | 185 mm² |  | 0 | 0 | 0 | 0 | [8 empty] | Total Load R: 206; Total Load Y: 163; Total Load B: 209; Total Load N: 61 | 209 | 163 | 31.0595 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN3 | 23.192684, 56.488828 | 1431 | Ground (GMT) | 3 | 1000 | 12/06/2026, 15:20 | 1 | 238 | 239 | 241 | 416 | 417 | 420 | 185 mm² |  | 25 | 33 | 3 | 20 | 185 mm² |  | 12 | 27 | 17 | 14 | 185 mm² |  | 15 | 25 | 13 | 9 | 185 mm² |  | 55 | 128 | 76 | 42 | [20 empty] | Total Load R: 107; Total Load Y: 213; Total Load B: 109; Total Load N: 85 | 213 | 107 | 15.3474 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN2 | 23.208523, 56.524778 | 319 | Ground (GMT) | 3 | 1000 | 12/06/2026, 15:17 | 1 | 242 | 245 | 249 | 422 | 421 | 420 | 185 mm² |  | 53 | 56 | 25 | 18 | 185 mm² |  | 68 | 81 | 92 | 25 | 185 mm² |  | 36 | 85 | 48 | 42 | [26 empty] | Total Load R: 157; Total Load Y: 222; Total Load B: 165; Total Load N: 85 | 222 | 157 | 16.2265 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.196168, 56.489364 | 462 | Ground (GMT) | 3 | 1000 | 12/06/2026, 15:13 | 1 | 237 | 237 | 240 | 410 | 416 | 413 | [18 empty] | 185 mm² |  | 40 | 39 | 20 | 17 | 185 mm² |  | 205 | 125 | 106 | 60 | 185 mm² |  | 175 | 221 | 212 | 40 | [6 empty] | 120 mm² |  | 103 | 126 | 100 | 50 | 523 | 511 | 438 | 167 | 523 | 438 | 37.1404 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN2 | 23.210646, 56.522809 | 1500 | Pole (PMT) | 3 | 315 | 12/06/2026, 15:13 | 1 | 250 | 249 | 248 | 438 | 436 | 439 | 185 mm² |  | 45 | 70 | 46 | 26 | [38 empty] | Total Load R: 45; Total Load Y: 70; Total Load B: 46; Total Load N: 26 | 70 | 45 | 16.8586 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.193823, 56.492674 | 1649 | Ground (GMT) | 3 | 500 | 12/06/2026, 15:05 | 1 | 238 | 239 | 241 | 411 | 418 | 417 | [18 empty] | 185 mm² |  | 103 | 51 | 100 | 61 | 185 mm² |  | 50 | 38 | 46 | 22 | 185 mm² |  | 51 | 49 | 22 | 35 | [8 empty] | Total Load R: 204; Total Load Y: 138; Total Load B: 168; Total Load N: 118 | 204 | 138 | 29.0444 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN1 | 23.215949, 56.51359 | 309 | Ground (GMT) | 3 | 1000 | 12/06/2026, 15:04 | 1 | 240 | 241 | 240 | 421 | 419 | 422 | 185 mm² |  | 55 | 36 | 41 | 18 | [12 empty] | 185 mm² |  | 98 | 102 | 71 | 21 | 240 mm² |  | 55 | 33 | 16 | 19 | 240 mm² |  | 42 | 56 | 28 | 16 | 120 mm² |  | 85 | 62 | 65 | 23 | 120 mm² |  | 68 | 48 | 92 | 42 | 403 | 337 | 313 | 139 | 403 | 313 | 29.3865 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN1 | 23.217523, 56.511099 | 1679 | Ground (GMT) | 3 | 1000 | 12/06/2026, 14:54 | 1 | 240 | 241 | 240 | 424 | 422 | 421 | 185 mm² |  | 60 | 48 | 49 | 21 | 185 mm² |  | 70 | 29 | 31 | 18 | [12 empty] | 185 mm² |  | 99 | 103 | 156 | 48 | [14 empty] | Total Load R: 229; Total Load Y: 180; Total Load B: 236; Total Load N: 87 | 236 | 180 | 17.3316 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN1 | 23.219141, 56.510931 | 114 | Pole (PMT) | 3 | 315 | 12/06/2026, 14:50 | 1 | 240 | 241 | 242 | 421 | 419 | 422 | 120 mm² |  | 110 | 131 | 131 | 51 | 120 mm² |  | 15 | 6 | 22 | 11 | [32 empty] | Total Load R: 125; Total Load Y: 137; Total Load B: 153; Total Load N: 62 | 153 | 125 | 35.418 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.187542, 56.487813 | 1492 | Ground (GMT) | 3 | 1000 | 12/06/2026, 14:47 | 1 | 239 | 239 | 239 | 413 | 419 | 417 | [18 empty] | 185 mm² |  | 65 | 62 | 144 | 43 | 185 mm² |  | 33 | 29 | 35 | 6 | 185 mm² |  | 60 | 68 | 101 | 34 | 185 mm² |  | 74 | 42 | 12 | 46 |  |  | Total Load R: 232; Total Load Y: 201; Total Load B: 292; Total Load N: 129 | 292 | 201 | 20.8878 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN1 | 23.218494, 56.503881 | 113 | Ground (GMT) | 3 | 500 | 12/06/2026, 14:42 | 1 | 241 | 241 | 242 | 419 | 419 | 420 | [6 empty] | 240 mm² |  | 101 | 65 | 51 | 34 | 240 mm² |  | 96 | 85 | 208 | 35 | 185 mm² |  | 38 | 76 | 58 | 13 | [20 empty] | Total Load R: 235; Total Load Y: 226; Total Load B: 317; Total Load N: 82 | 317 | 226 | 46.0112 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.18824, 56.489933 | 464 | Ground (GMT) | 3 | 1000 | 12/06/2026, 14:41 | 1 | 239 | 242 | 240 | 416 | 412 | 419 | 185 mm² |  | 96 | 69 | 128 | 43 | 185 mm² |  | 60 | 54 | 75 | 18 | 185 mm² |  | 8 | 6 | 6 | 10 | [26 empty] | Total Load R: 164; Total Load Y: 129; Total Load B: 209; Total Load N: 71 | 209 | 129 | 15.0591 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN1 | 23.217664, 56.502685 | 1916 | Ground (GMT) | 3 | 1000 | 12/06/2026, 14:38 | 1 | 247 | 246 | 249 | 426 | 431 | 430 | [6 empty] | 240 mm² |  | 210 | 104 | 231 | 3 | 240 mm² | [5 empty] | 240 mm² | [5 empty] | 240 mm² |  | 15 | 125 | 117 | 17 | [14 empty] | Total Load R: 225; Total Load Y: 229; Total Load B: 348; Total Load N: 20 | 348 | 225 | 25.6773 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.191021, 56.497714 | 2110 | Pole (PMT) | 3 | 315 | 12/06/2026, 14:28 | 1 | 238 | 235 | 240 | 410 | 416 | 411 | 185 mm² |  | 21 | 63 | 9 | 51 | 185 mm² |  | 50 | 140 | 96 | 52 | [32 empty] | Total Load R: 71; Total Load Y: 203; Total Load B: 105; Total Load N: 103 | 203 | 71 | 45.7646 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN1 | 23.219258, 56.499432 | 112 | Ground (GMT) | 3 | 1000 | 12/06/2026, 14:28 | 1 | 245 | 242 | 243 | 422 | 416 | 421 | 185 mm² |  | 25 | 26 | 11 | 16 | 185 mm² |  | 33 | 25 | 15 | 19 | 185 mm² |  | 16 | 26 | 55 | 28 | 185 mm² |  | 85 | 56 | 140 | 48 | 240 mm² | [19 empty] | Total Load R: 159; Total Load Y: 133; Total Load B: 221; Total Load N: 111 | 221 | 133 | 16.1535 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.191388, 56.496845 | 479 | Pole (PMT) | 3 | 315 | 12/06/2026, 14:22 | 1 | 242 | 242 | 246 | 418 | 424 | 423 | 120 mm² |  | 125 | 114 | 62 | 46 | 120 mm² |  | 27 | 56 | 60 | 41 | [32 empty] | Total Load R: 152; Total Load Y: 170; Total Load B: 122; Total Load N: 87 | 170 | 122 | 39.0729 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.186967, 56.495385 | 478 | Pole (PMT) | 3 | 315 | 12/06/2026, 14:18 | 1 | 247 | 245 | 242 | 413 | 412 | 411 | 120 mm² |  | 83 | 58 | 35 | 34 | 120 mm² |  | 122 | 77 | 91 | 40 | [32 empty] | Total Load R: 205; Total Load Y: 135; Total Load B: 126; Total Load N: 74 | 205 | 126 | 46.5537 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN1 | 23.218771, 56.498418 | 110 | Ground (GMT) | 3 | 1000 | 12/06/2026, 14:21 | 1 | 244 | 244 | 247 | 423 | 417 | 422 | 120 mm² |  | 6 | 18 | 33 | 13 | 240 mm² |  | 72 | 45 | 26 | 19 | 185 mm² |  | 29 | 89 | 33 | 16 | 185 mm² |  | 78 | 46 | 48 | 25 | 120 mm² |  | 98 | 56 | 98 | 41 | 185 mm² |  | 115 | 75 | 72 | 46 | 185 mm² |  | 60 | 85 | 88 | 45 | 185 mm² |  | Total Load R: 458; Total Load Y: 414; Total Load B: 398; Total Load N: 205 | 458 | 398 | 33.5557 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN3 | 23.186086, 56.493371 | 165 | Ground (GMT) | 3 | 500 | 12/06/2026, 14:13 | 1 | 234 | 234 | 237 | 403 | 409 | 412 | [18 empty] | 185 mm² | [5 empty] | 185 mm² |  | 59 | 72 | 126 | 54 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 113 | 76 | 105 | 11 |  |  | Total Load R: 172; Total Load Y: 148; Total Load B: 231; Total Load N: 65 | 231 | 148 | 32.2484 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN1 | 23.217711, 56.50076 | 4262 | Ground (GMT) | 3 | 1000 | 12/06/2026, 14:12 | 1 | 242 | 240 | 243 | 424 | 425 | 429 | [12 empty] | 185 mm² |  | 61 | 72 | 28 | 26 | [12 empty] | 240 mm² |  | 21 | 15 | 12 | 17 | 240 mm² |  | 45 | 48 | 25 | 21 |  |  | Total Load R: 127; Total Load Y: 135; Total Load B: 65; Total Load N: 64 | 135 | 65 | 9.9143 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN1 | 23.218335, 56.49421 | 1651 | Ground (GMT) | 3 | 500 | 12/06/2026, 14:06 | 1 | 241 | 242 | 240 | 421 | 420 | 422 | 240 mm² |  | 35 | 52 | 65 | 60 | 120 mm² |  | 11 | 20 | 15 | 14 | 185 mm² |  | 31 | 52 | 140 | 20 | 120 mm² |  | 120 | 105 | 108 | 40 | 185 mm² |  | 11 | 25 | 18 | 12 | 185 mm² |  | 29 | 40 | 39 | 17 | [8 empty] | Total Load R: 237; Total Load Y: 294; Total Load B: 385; Total Load N: 163 | 385 | 237 | 56.1479 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.177958, 56.495468 | 1990 | Pole (PMT) | 3 | 315 | 11/06/2026, 15:23 | 1 | 239 | 238 | 237 | 414 | 413 | 410 | 185 mm² |  | 31 | 21 | 46 | 13 | [38 empty] | Total Load R: 31; Total Load Y: 21; Total Load B: 46; Total Load N: 13 | 46 | 21 | 10.4715 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.182688, 56.489865 | 1823 | Ground (GMT) | 3 | 500 | 11/06/2026, 15:15 | 1 | 240 | 238 | 237 | 416 | 415 | 411 | [18 empty] | 120 mm² |  | 10 | 3 | 23 | 16 | 120 mm² |  | 13 | 7 | 12 | 5 | [14 empty] | Total Load R: 23; Total Load Y: 10; Total Load B: 35; Total Load N: 21 | 35 | 10 | 5.0437 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.180177, 56.494824 | 465 | Pole (PMT) | 3 | 315 | 11/06/2026, 15:05 | 1 | 251 | 250 | 249 | 436 | 433 | 431 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 55 | 55 | 111 | 47 | [32 empty] | Total Load R: 55; Total Load Y: 55; Total Load B: 111; Total Load N: 47 | 111 | 55 | 26.6109 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.180161, 56.494908 | 1363 | Pole (PMT) | 3 | 315 | 11/06/2026, 15:01 | 1 | 235 | 235 | 37 | 408 | 409 | 406 | 120 mm² |  | 143 | 46 | 109 | 12 | 120 mm² |  | 143 | 93 | 94 | 54 | [32 empty] | Total Load R: 286; Total Load Y: 139; Total Load B: 203; Total Load N: 66 | 286 | 139 | 64.1618 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.173153, 56.486337 | 1918 | Pole (PMT) | 3 | 315 | 11/06/2026, 14:47 | 1 | 239 | 237 | 237 | 415 | 415 | 414 | 185 mm² |  | 47 | 75 | 36 | 28 | 185 mm² |  | 13 | 9 | 20 | 11 | [32 empty] | Total Load R: 60; Total Load Y: 84; Total Load B: 56; Total Load N: 39 | 84 | 56 | 19.168 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.179354, 56.490583 | 466 | Ground (GMT) | 3 | 500 | 11/06/2026, 14:41 | 1 | 238 | 237 | 237 | 412 | 413 | 409 | 185 mm² |  | 58 | 44 | 34 | 15 | 185 mm² |  | 91 | 122 | 102 | 35 | 185 mm² |  | 18 | 32 | 44 | 26 | 185 mm² |  | 127 | 78 | 99 | 25 | 185 mm² |  | 1 | 0 | 7 | 2 | [14 empty] | Total Load R: 295; Total Load Y: 276; Total Load B: 286; Total Load N: 103 | 295 | 276 | 42.1027 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN3 | 23.174002, 56.489489 | 467 | Pole (PMT) | 3 | 315 | 11/06/2026, 14:33 | 1 | 237 | 235 | 234 | 410 | 407 | 406 | 120 mm² |  | 105 | 126 | 142 | 29 | 120 mm² |  | 58 | 34 | 38 | 22 | [32 empty] | Total Load R: 163; Total Load Y: 160; Total Load B: 180; Total Load N: 51 | 180 | 160 | 40.5795 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN3 | 23.169691, 56.499861 | 468 | Pole (PMT) | 3 | 100 | 11/06/2026, 14:26 | 1 | 232 | 237 | 239 | 410 | 411 | 406 | 120 mm² |  | 38 | 23 | 13 | 16 | 50 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 38; Total Load Y: 23; Total Load B: 13; Total Load N: 16 | 38 | 13 | 26.9854 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.171597, 56.501446 | 1994 | Pole (PMT) | 3 | 100 | 11/06/2026, 14:27 | 1 | 240 | 238 | 237 | 417 | 415 | 410 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN3 | 23.195466, 56.495038 | 1949 | Ground (GMT) |  | 1000 | 30/05/2026, 15:24 | 1 | 241 | 240 | 243 | 416 | 422 | 420 | [12 empty] | 185 mm² |  | 52 | 94 | 69 | 22 | 185 mm² |  | 19 | 15 | 16 | 7 | 185 mm² |  | 44 | 50 | 81 | 27 | 185 mm² |  | 90 | 75 | 27 | 64 | 185 mm² |  | 8 | 1 | 8 | 6 |  |  | Total Load R: 213; Total Load Y: 235; Total Load B: 201; Total Load N: 126 | 235 | 201 | 16.9325 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN3 | 23.197338, 56.498579 | 2305 | Ground (GMT) |  | 1000 | 30/05/2026, 15:14 | 1 | 238 | 240 | 242 | 413 | 417 | 419 | [24 empty] | 185 mm² |  | 86 | 68 | 127 | 101 | 185 mm² |  | 88 | 80 | 33 | 55 | 185 mm² |  | 101 | 70 | 73 | 25 | 185 mm² |  | 0 | 10 | 16 | 12 | 275 | 228 | 249 | 193 | 275 | 228 | 19.6718 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN3 | 23.196642, 56.497646 | 1707 | Ground (GMT) |  | 1000 | 30/05/2026, 15:04 | 1 | 240 | 239 | 242 | 413 | 421 | 418 | 185 mm² |  | 116 | 101 | 98 | 26 | 185 mm² |  | 70 | 127 | 78 | 32 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 3 | 14 | 11 | 16 | 185 mm² |  | 153 | 114 | 117 | 42 | 185 mm² |  | 55 | 72 | 56 | 27 | 185 mm² |  | 0 | 0 | 0 | 0 |  |  | Total Load R: 397; Total Load Y: 428; Total Load B: 360; Total Load N: 143 | 428 | 360 | 30.6164 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN3 | 23.200468, 56.493091 | 459 | Ground (GMT) |  | 1000 | 30/05/2026, 14:54 | 1 | 239 | 238 | 242 | 411 | 419 | 416 | [6 empty] | 185 mm² |  | 12 | 0 | 3 | 12 | 185 mm² |  | 124 | 229 | 151 | 38 | 185 mm² |  | 113 | 48 | 38 | 38 | 185 mm² |  | 112 | 105 | 125 | 20 | 185 mm² |  | 128 | 156 | 126 | 56 | 185 mm² |  | 40 | 55 | 70 | 22 | 185 mm² |  | 78 | 84 | 72 | 17 | 607 | 677 | 585 | 203 | 677 | 585 | 48.1938 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN3 | 23.200198, 56.498412 | 461 | Ground (GMT) |  | 1000 | 30/05/2026, 14:43 | 1 | 240 | 241 | 243 | 414 | 418 | 422 | 185 mm² |  | 5 | 12 | 24 | 22 | 185 mm² |  | 71 | 60 | 76 | 16 | [12 empty] | 185 mm² |  | 164 | 148 | 174 | 27 | 185 mm² |  | 170 | 199 | 176 | 19 | 185 mm² |  | 26 | 19 | 9 | 12 | 185 mm² |  | 153 | 146 | 111 | 48 | 589 | 584 | 570 | 144 | 589 | 570 | 42.2354 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN3 | 23.203543, 56.497092 | 1416 | Ground (GMT) |  | 1000 | 30/05/2026, 14:33 | 1 | 244 | 423 | 247 | 420 | 427 | 425 | [24 empty] | 185 mm² |  | 10 | 70 | 35 | 41 | 185 mm² |  | 96 | 59 | 71 | 31 | 240 mm² |  | 50 | 62 | 34 | 27 |  |  | Total Load R: 156; Total Load Y: 191; Total Load B: 140; Total Load N: 99 | 191 | 140 | 13.8945 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.204786, 56.497894 | 300 | Ground (GMT) |  | 1000 | 30/05/2026, 14:27 | 1 | 243 | 243 | 247 | 419 | 426 | 425 | 185 mm² |  | 168 | 108 | 140 | 64 | 185 mm² |  | 54 | 50 | 44 | 11 | [12 empty] | 185 mm² |  | 79 | 38 | 33 | 35 | 185 mm² |  | 131 | 83 | 57 | 53 | 185 mm² |  | 1 | 9 | 18 | 11 |  |  | Total Load R: 433; Total Load Y: 288; Total Load B: 292; Total Load N: 174 | 433 | 288 | 31.4241 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.216968, 56.502388 | 1455 | Ground (GMT) |  | 1000 | 30/05/2026, 14:15 | 1 | 247 | 246 | 250 | 426 | 432 | 430 | 70 mm² |  | 11 | 11 | 0 | 10 | 185 mm² |  | 10 | 10 | 11 | 5 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 252 | 230 | 193 | 69 | 185 mm² |  | 2 | 11 | 41 | 21 | 185 mm² |  | 22 | 32 | 7 | 23 | [6 empty] | 240 mm² |  | 0 | 0 | 0 | 0 | 297 | 294 | 252 | 128 | 297 | 252 | 21.9143 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN3 | 23.217404, 56.501765 | 1870 | Ground (GMT) |  | 1000 | 30/05/2026, 14:04 | 1 | 245 | 244 | 247 | 422 | 428 | 426 | 240 mm² |  | 39 | 14 | 40 | 32 | 240 mm² |  | 65 | 30 | 37 | 29 | [32 empty] | Total Load R: 104; Total Load Y: 44; Total Load B: 77; Total Load N: 61 | 104 | 44 | 7.6016 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.217468, 56.501448 | 295 | Ground (GMT) |  | 1000 | 30/05/2026, 13:59 | 1 | 243 | 242 | 245 | 417 | 425 | 423 | [30 empty] | 70 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 225 | 124 | 124 | 80 | 185 mm² |  | 31 | 0 | 33 | 15 | 256 | 124 | 157 | 95 | 256 | 124 | 18.49 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.217733, 56.499259 | 1546 | Ground (GMT) |  | 1000 | 30/05/2026, 13:53 | 1 | 244 | 243 | 246 | 421 | 427 | 424 | [6 empty] | 120 mm² |  | 25 | 19 | 24 | 7 | 185 mm² |  | 31 | 31 | 9 | 28 | 185 mm² |  | 85 | 0 | 27 | 81 | [20 empty] | Total Load R: 141; Total Load Y: 50; Total Load B: 60; Total Load N: 116 | 141 | 50 | 10.2816 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.210058, 56.499614 | 299 | Ground (GMT) |  | 1000 | 21/05/2026, 12:32 | 1 | 246 | 245 | 249 | 425 | 432 | 429 | [6 empty] | 185 mm² |  | 86 | 70 | 30 | 48 | 185 mm² |  | 62 | 17 | 10 | 24 | 185 mm² |  | 32 | 48 | 4 | 47 | 185 mm² |  | 12 | 13 | 24 | 7 | 185 mm² |  | 43 | 22 | 24 | 16 | [8 empty] | Total Load R: 235; Total Load Y: 170; Total Load B: 92; Total Load N: 142 | 235 | 92 | 17.2989 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN3 | 23.210058, 56.499614 | 299 | Ground (GMT) |  | 1000 | 30/05/2026, 14:22 | 2 | 245 | 244 | 248 | 422 | 428 | 427 | [6 empty] | 185 mm² |  | 50 | 105 | 30 | 55 | 185 mm² |  | 132 | 46 | 64 | 77 | 185 mm² |  | 50 | 22 | 79 | 42 | 185 mm² |  | 21 | 46 | 28 | 22 | 185 mm² |  | 51 | 4 | 11 | 39 | [8 empty] | Total Load R: 304; Total Load Y: 223; Total Load B: 212; Total Load N: 235 | 304 | 212 | 22.2201 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN2 |  | 1851 | Ground (GMT) |  | 500 | 03/05/2026, 12:27 | 1 | 248 | 247 | 251 | 426 | 431 | 433 | 240 mm² |  | 96 | 56 | 55 | 35 | 240 mm² |  | 70 | 53 | 76 | 45 | 240 mm² |  | 45 | 171 | 151 | 58 | [26 empty] | Total Load R: 211; Total Load Y: 280; Total Load B: 282; Total Load N: 138 | 282 | 211 | 41.6149 | OK - No Upgrade | OK - Balanced
Ibri | SULAIF | K_LN2 |  | 314 | Ground (GMT) |  | 500 | 03/05/2026, 12:27 | 1 | 248 | 249 | 252 | 430 | 436 | 427 | 240 mm² |  | 41 | 51 | 56 | 75 | 240 mm² |  | 222 | 138 | 129 | 70 | 240 mm² |  | 65 | 70 | 73 | 85 | [26 empty] | Total Load R: 328; Total Load Y: 259; Total Load B: 258; Total Load N: 230 | 328 | 258 | 48.8577 | OK - No Upgrade | Need to Balance
Ibri | SULAIF | K_LN2 |  | 313 | Ground (GMT) |  | 500 | 03/05/2026, 12:27 | 1 | 248 | 248 | 251 | 429 | 432 | 434 | 240 mm² |  | 195 | 120 | 129 | 66 | 240 mm² |  | 113 | 105 | 150 | 70 | [32 empty] | Total Load R: 308; Total Load Y: 225; Total Load B: 279; Total Load N: 136 | 308 | 225 | 45.7719 | OK - No Upgrade | Need to Balance

## AL-MURTAFA
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Feeder 9 | [5 empty] | Feeder 10 | [5 empty] | Feeder 11 | [5 empty] | Feeder 12 | [5 empty] | Feeder 13 | [5 empty] | Feeder 14 | [5 empty] | Feeder 15 | [5 empty] | Feeder 16 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Ibri | AL-MURTAFA | K_LN3 | 23.209002, 56.530882 | 340 | Pole (PMT) | 3 | 315 | 10/06/2026, 22:37 | 1 | 251 | 248 | 247 | 433 | 432 | 429 | 185 mm² |  | 39 | 22 | 23 | 10 | 185 mm² |  | 18 | 11 | 9 | 4 | [80 empty] | Total Load R: 57; Total Load Y: 33; Total Load B: 32; Total Load N: 14 | 57 | 32 | 13.571 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN4 | 23.226277, 56.519505 | 282 | Ground (GMT) | 3 | 1000 | 09/06/2026, 21:47 | 1 | 240 | 240 | 243 | 414 | 420 | 418 | [6 empty] | 185 mm² |  | 62 | 109 | 101 | 30 | 185 mm² |  | 101 | 45 | 83 | 48 | 185 mm² |  | 27 | 8 | 3 | 16 | 185 mm² |  | 88 | 100 | 47 | 23 | [62 empty] | Total Load R: 278; Total Load Y: 262; Total Load B: 234; Total Load N: 117 | 278 | 234 | 19.9345 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN4 | 23.226277, 56.519505 | 282 | Ground (GMT) | 3 | 1000 | 09/06/2026, 21:04 | 2 | 248 | 247 | 249 | 428 | 433 | 430 | 185 mm² |  | 113 | 56 | 54 | 44 | 185 mm² |  | 82 | 104 | 145 | 47 | 185 mm² |  | 100 | 106 | 47 | 50 | [6 empty] | 185 mm² |  | 20 | 48 | 11 | 31 | [62 empty] | Total Load R: 315; Total Load Y: 314; Total Load B: 257; Total Load N: 172 | 315 | 257 | 23.3515 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN7 | 23.223047, 56.504572 | 1374 | Pole (PMT) | 3 | 315 | 06/06/2026, 14:37 | 1 | 241 | 241 | 240 | 419 | 417 | 416 | 120 mm² |  | 187 | 88 | 78 | 72 | 185 mm² |  | 0 | 17 | 16 | 22 | [80 empty] | Total Load R: 187; Total Load Y: 105; Total Load B: 94; Total Load N: 94 | 187 | 94 | 43.083 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.223047, 56.504572 | 1374 | Pole (PMT) | 3 | 315 | 10/06/2026, 22:39 | 2 | 246 | 245 | 245 | 426 | 426 | 425 | 120 mm² |  | 106 | 82 | 45 | 23 | 185 mm² |  | 2 | 1 | 4 | 6 | [80 empty] | Total Load R: 108; Total Load Y: 83; Total Load B: 49; Total Load N: 29 | 108 | 49 | 25.2978 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.224378, 56.505688 | 2032 | Pole (PMT) | 3 | 315 | 06/06/2026, 14:33 | 1 | 242 | 241 | 243 | 418 | 422 | 419 | 185 mm² |  | 94 | 75 | 88 | 26 | 185 mm² |  | 1 | 13 | 17 | 17 | [80 empty] | Total Load R: 95; Total Load Y: 88; Total Load B: 105; Total Load N: 43 | 105 | 88 | 24.1332 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN7 | 23.224378, 56.505688 | 2032 | Pole (PMT) | 3 | 315 | 10/06/2026, 22:36 | 2 | 247 | 245 | 246 | 427 | 428 | 426 | 185 mm² |  | 44 | 60 | 62 | 9 | 185 mm² |  | 3 | 33 | 54 | 49 | [80 empty] | Total Load R: 47; Total Load Y: 93; Total Load B: 116; Total Load N: 58 | 116 | 47 | 27.2355 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.230172, 56.504465 | 1789 | Pole (PMT) | 3 | 315 | 06/06/2026, 14:29 | 1 | 243 | 242 | 243 | 420 | 422 | 420 | 185 mm² |  | 28 | 32 | 77 | 46 | 185 mm² |  | 14 | 26 | 29 | 20 | [80 empty] | Total Load R: 42; Total Load Y: 58; Total Load B: 106; Total Load N: 66 | 106 | 42 | 24.4797 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.230172, 56.504465 | 1789 | Pole (PMT) | 3 | 315 | 10/06/2026, 22:49 | 2 | 247 | 244 | 245 | 427 | 425 | 425 | 185 mm² |  | 17 | 51 | 95 | 64 | 185 mm² |  | 2 | 42 | 25 | 41 | [80 empty] | Total Load R: 19; Total Load Y: 93; Total Load B: 120; Total Load N: 105 | 120 | 19 | 28.1747 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.226519, 56.50523 | 8 | Pole (PMT) | 3 | 315 | 06/06/2026, 14:24 | 1 | 242 | 238 | 242 | 417 | 420 | 416 | 185 mm² |  | 30 | 72 | 45 | 36 | 185 mm² |  | 24 | 81 | 74 | 47 | [80 empty] | Total Load R: 54; Total Load Y: 153; Total Load B: 119; Total Load N: 83 | 153 | 54 | 35.0815 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.226519, 56.50523 | 8 | Pole (PMT) | 3 | 315 | 10/06/2026, 22:45 | 2 | 244 | 240 | 242 | 423 | 421 | 415 | 185 mm² |  | 24 | 86 | 9 | 58 | 120 mm² |  | 76 | 160 | 180 | 88 | [80 empty] | Total Load R: 100; Total Load Y: 246; Total Load B: 189; Total Load N: 146 | 246 | 100 | 57.2171 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.226938, 56.51013 | 9 | Pole (PMT) | 3 | 315 | 06/06/2026, 14:21 | 1 | 242 | 240 | 242 | 416 | 421 | 418 | 120 mm² |  | 53 | 68 | 43 | 12 | 185 mm² |  | 32 | 34 | 71 | 39 | [80 empty] | Total Load R: 85; Total Load Y: 102; Total Load B: 114; Total Load N: 51 | 114 | 85 | 26.0764 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.226938, 56.51013 | 9 | Pole (PMT) | 3 | 315 | 10/06/2026, 22:31 | 2 | 246 | 244 | 246 | 425 | 427 | 425 | 120 mm² |  | 56 | 91 | 62 | 27 | 185 mm² |  | 27 | 32 | 69 | 40 | [80 empty] | Total Load R: 83; Total Load Y: 123; Total Load B: 131; Total Load N: 67 | 131 | 83 | 30.6133 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.231113, 56.506805 | 1977 | Pole (PMT) | 3 | 315 | 06/06/2026, 14:16 | 1 | 241 | 239 | 241 | 416 | 418 | 415 | 185 mm² |  | 69 | 68 | 73 | 14 | 185 mm² |  | 73 | 67 | 108 | 29 | [80 empty] | Total Load R: 142; Total Load Y: 135; Total Load B: 181; Total Load N: 43 | 181 | 135 | 41.4021 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.231113, 56.506805 | 1977 | Pole (PMT) | 3 | 315 | 10/06/2026, 22:13 | 2 | 247 | 245 | 246 | 427 | 428 | 427 | 185 mm² |  | 27 | 23 | 36 | 20 | 185 mm² |  | 42 | 55 | 100 | 44 | [80 empty] | Total Load R: 69; Total Load Y: 78; Total Load B: 136; Total Load N: 64 | 136 | 69 | 31.9313 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.234213, 56.507509 | 4349 | Pole (PMT) | 3 | 315 | 06/06/2026, 14:09 | 1 | 239 | 239 | 243 | 413 | 421 | 416 | 240 mm² |  | 65 | 65 | 42 | 24 | 240 mm² |  | 110 | 84 | 59 | 39 | [80 empty] | Total Load R: 175; Total Load Y: 149; Total Load B: 101; Total Load N: 63 | 175 | 101 | 39.7409 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.234213, 56.507509 | 4349 | Pole (PMT) | 3 | 315 | 10/06/2026, 22:23 | 2 | 244 | 243 | 247 | 423 | 427 | 424 | 185 mm² |  | 36 | 26 | 0 | 27 | 185 mm² |  | 120 | 124 | 74 | 53 | [80 empty] | Total Load R: 156; Total Load Y: 150; Total Load B: 74; Total Load N: 80 | 156 | 74 | 36.284 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.230605, 56.509516 | 1376 | Pole (PMT) | 3 | 315 | 06/06/2026, 14:05 | 1 | 241 | 240 | 243 | 417 | 422 | 418 | 185 mm² |  | 49 | 71 | 53 | 22 | 185 mm² |  | 45 | 40 | 63 | 20 | 185 mm² |  | 89 | 44 | 10 | 62 | [74 empty] | Total Load R: 183; Total Load Y: 155; Total Load B: 126; Total Load N: 104 | 183 | 126 | 41.9602 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.230605, 56.509516 | 1376 | Pole (PMT) | 3 | 315 | 10/06/2026, 22:18 | 2 | 246 | 245 | 247 | 426 | 428 | 427 | 185 mm² |  | 13 | 11 | 35 | 16 | 185 mm² |  | 36 | 16 | 47 | 24 | 185 mm² |  | 71 | 41 | 15 | 44 | [74 empty] | Total Load R: 120; Total Load Y: 68; Total Load B: 97; Total Load N: 84 | 120 | 68 | 28.1087 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.229485, 56.511476 | 10 | Pole (PMT) | 3 | 315 | 06/06/2026, 14:01 | 1 | 241 | 243 | 239 | 419 | 417 | 412 | 185 mm² |  | 112 | 18 | 92 | 86 | 185 mm² |  | 138 | 63 | 145 | 77 | [80 empty] | Total Load R: 250; Total Load Y: 81; Total Load B: 237; Total Load N: 163 | 250 | 81 | 57.5976 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.229485, 56.511476 | 10 | Pole (PMT) | 3 | 315 | 10/06/2026, 22:08 | 2 | 245 | 246 | 243 | 426 | 423 | 426 | 185 mm² |  | 125 | 83 | 132 | 46 | 185 mm² |  | 81 | 44 | 78 | 41 | [80 empty] | Total Load R: 206; Total Load Y: 127; Total Load B: 210; Total Load N: 87 | 210 | 127 | 49.1902 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.230117, 56.511859 | 11 | Ground (GMT) | 3 | 1000 | 06/06/2026, 13:57 | 1 | 243 | 243 | 244 | 421 | 424 | 423 | [6 empty] | 120 mm² |  | 41 | 155 | 138 | 74 | 120 mm² |  | 40 | 29 | 56 | 25 | 120 mm² |  | 91 | 27 | 38 | 56 | 185 mm² |  | 86 | 74 | 101 | 54 | 240 mm² |  | 79 | 95 | 84 | 45 | 240 mm² |  | 84 | 23 | 25 | 35 | [50 empty] | Total Load R: 421; Total Load Y: 403; Total Load B: 442; Total Load N: 289 | 442 | 403 | 32.2303 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN7 | 23.230117, 56.511859 | 11 | Ground (GMT) | 3 | 1000 | 10/06/2026, 23:02 | 2 | 245 | 246 | 243 | 424 | 425 | 421 | [6 empty] | 185 mm² |  | 83 | 181 | 83 | 72 | 120 mm² |  | 13 | 43 | 42 | 38 | 185 mm² |  | 87 | 51 | 92 | 29 | 120 mm² |  | 36 | 139 | 67 | 59 | 185 mm² |  | 42 | 103 | 88 | 38 | 185 mm² |  | 52 | 37 | 36 | 22 | [50 empty] | Total Load R: 313; Total Load Y: 554; Total Load B: 408; Total Load N: 258 | 554 | 313 | 40.6852 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.23188, 56.513334 | 12 | Ground (GMT) | 3 | 1000 | 06/06/2026, 13:50 | 1 | 244 | 243 | 245 | 423 | 426 | 424 | 120 mm² |  | 66 | 67 | 59 | 23 | [6 empty] | 120 mm² |  | 74 | 107 | 56 | 46 | 185 mm² |  | 47 | 44 | 86 | 28 | 185 mm² |  | 73 | 116 | 138 | 54 | [6 empty] | 185 mm² |  | 28 | 79 | 101 | 76 | 120 mm² |  | 80 | 118 | 114 | 25 | [44 empty] | Total Load R: 368; Total Load Y: 531; Total Load B: 554; Total Load N: 252 | 554 | 368 | 40.5892 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.23188, 56.513334 | 12 | Ground (GMT) | 3 | 1000 | 10/06/2026, 22:02 | 2 | 248 | 246 | 247 | 425 | 426 | 428 | 120 mm² |  | 115 | 131 | 190 | 69 | [6 empty] | 120 mm² |  | 105 | 137 | 92 | 38 | 185 mm² |  | 31 | 57 | 94 | 45 | 185 mm² |  | 54 | 76 | 86 | 27 | [6 empty] | 185 mm² |  | 63 | 77 | 99 | 31 | 120 mm² |  | 80 | 52 | 128 | 51 | [44 empty] | Total Load R: 448; Total Load Y: 530; Total Load B: 689; Total Load N: 261 | 689 | 448 | 50.7188 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.231784, 56.514809 | 13 | Ground (GMT) | 3 | 1000 | 06/06/2026, 13:39 | 1 | 245 | 245 | 247 | 423 | 429 | 428 | [12 empty] | 120 mm² |  | 148 | 59 | 85 | 24 | [6 empty] | 120 mm² |  | 133 | 127 | 200 | 52 | 120 mm² |  | 83 | 108 | 66 | 23 | 185 mm² |  | 25 | 1 | 2 | 26 | [50 empty] | Total Load R: 389; Total Load Y: 295; Total Load B: 353; Total Load N: 125 | 389 | 295 | 28.5004 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN7 | 23.231784, 56.514809 | 13 | Ground (GMT) | 3 | 1000 | 10/06/2026, 23:10 | 2 | 245 | 243 | 246 | 426 | 424 | 422 | [12 empty] | 120 mm² |  | 138 | 166 | 42 | 27 | [6 empty] | 120 mm² |  | 81 | 146 | 261 | 138 | 120 mm² |  | 124 | 190 | 66 | 89 | 185 mm² |  | 23 | 0 | 13 | 21 | [50 empty] | Total Load R: 366; Total Load Y: 502; Total Load B: 382; Total Load N: 275 | 502 | 366 | 37.0403 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.213651, 56.551409 | 341 | Pole (PMT) | 3 | 315 | 05/06/2026, 14:38 | 1 | 244 | 243 | 244 | 422 | 424 | 425 | 120 mm² |  | 46 | 34 | 103 | 62 | [86 empty] | Total Load R: 46; Total Load Y: 34; Total Load B: 103; Total Load N: 62 | 103 | 34 | 23.9001 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.213651, 56.551409 | 341 | Pole (PMT) | 3 | 315 | 10/06/2026, 22:07 | 2 | 249 | 247 | 244 | 431 | 433 | 415 | 120 mm² |  | 18 | 22 | 24 | 10 | [86 empty] | Total Load R: 18; Total Load Y: 22; Total Load B: 24; Total Load N: 10 | 24 | 18 | 5.6877 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.213826, 56.548851 | 2031 | Pole (PMT) | 3 | 315 | 05/06/2026, 14:31 | 1 | 244 | 243 | 246 | 422 | 427 | 423 | 185 mm² |  | 31 | 25 | 29 | 7 | 185 mm² |  | 0 | 12 | 12 | 12 | 185 mm² |  | 17 | 15 | 0 | 13 | [74 empty] | Total Load R: 48; Total Load Y: 52; Total Load B: 41; Total Load N: 32 | 52 | 41 | 12.0661 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.213826, 56.548851 | 2031 | Pole (PMT) | 3 | 315 | 10/06/2026, 22:16 | 2 | 248 | 247 | 249 | 428 | 431 | 429 | 185 mm² |  | 38 | 19 | 23 | 17 | 185 mm² |  | 0 | 12 | 12 | 9 | 185 mm² |  | 8 | 14 | 15 | 5 | [74 empty] | Total Load R: 46; Total Load Y: 45; Total Load B: 50; Total Load N: 31 | 50 | 45 | 11.7669 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN3 | 23.211015, 56.543314 | 336 | Ground (GMT) | 3 | 1000 | 05/06/2026, 14:24 | 1 | 244 | 243 | 246 | 421 | 426 | 424 | [6 empty] | 185 mm² |  | 28 | 24 | 39 | 11 | 185 mm² |  | 60 | 27 | 55 | 15 | 185 mm² |  | 129 | 79 | 57 | 52 | 185 mm² |  | 45 | 37 | 39 | 5 | [62 empty] | Total Load R: 262; Total Load Y: 167; Total Load B: 190; Total Load N: 83 | 262 | 167 | 19.1049 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.211015, 56.543314 | 336 | Ground (GMT) | 3 | 1000 | 10/06/2026, 22:20 | 2 | 248 | 247 | 248 | 428 | 430 | 429 | [6 empty] | 185 mm² |  | 30 | 52 | 44 | 8 | 185 mm² |  | 49 | 11 | 39 | 25 | 185 mm² |  | 35 | 75 | 53 | 28 | 185 mm² |  | 43 | 37 | 33 | 8 | [62 empty] | Total Load R: 157; Total Load Y: 175; Total Load B: 169; Total Load N: 69 | 175 | 157 | 12.9731 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN3 | 23.209277, 56.53789 | 338 | Ground (GMT) | 3 | 1000 | 05/06/2026, 14:17 | 1 | 245 | 244 | 246 | 421 | 428 | 426 | 185 mm² |  | 17 | 17 | 38 | 18 | 185 mm² |  | 110 | 68 | 128 | 74 | 185 mm² |  | 49 | 35 | 42 | 19 | 185 mm² |  | 92 | 48 | 83 | 41 | [68 empty] | Total Load R: 268; Total Load Y: 168; Total Load B: 291; Total Load N: 152 | 291 | 168 | 21.2195 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.209277, 56.53789 | 338 | Ground (GMT) | 3 | 1000 | 10/06/2026, 22:26 | 2 | 247 | 247 | 248 | 427 | 431 | 428 | 185 mm² |  | 33 | 42 | 17 | 20 | 185 mm² |  | 108 | 27 | 72 | 83 | 185 mm² |  | 29 | 59 | 26 | 30 | 185 mm² |  | 108 | 106 | 118 | 32 | [68 empty] | Total Load R: 278; Total Load Y: 234; Total Load B: 233; Total Load N: 165 | 278 | 233 | 20.5605 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.209449, 56.537614 | 339 | Pole (PMT) | 3 | 315 | 05/06/2026, 14:12 | 1 | 244 | 242 | 245 | 428 | 425 | 429 | 50 mm² |  | 10 | 0 | 2 | 9 | 185 mm² |  | 14 | 0 | 2 | 11 | [80 empty] | Total Load R: 24; Total Load Y: 0; Total Load B: 4; Total Load N: 20 | 24 | 0 | 5.6481 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.209449, 56.537614 | 339 | Pole (PMT) | 3 | 315 | 10/06/2026, 22:32 | 2 | 247 | 249 | 248 | 430 | 428 | 432 | 50 mm² |  | 3 | 1 | 3 | 3 | 185 mm² |  | 28 | 0 | 2 | 22 | [80 empty] | Total Load R: 31; Total Load Y: 1; Total Load B: 5; Total Load N: 25 | 31 | 1 | 7.3296 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 | 23.220709, 56.51406 | 134 | Ground (GMT) |  | 1000 | 05/06/2026, 14:04 | 1 | 244 | 243 | 246 | 420 | 426 | 423 | 185 mm² |  | 28 | 31 | 26 | 12 | 185 mm² |  | 65 | 75 | 97 | 28 | 185 mm² |  | 62 | 6 | 48 | 55 | 185 mm² |  | 38 | 60 | 20 | 30 | 185 mm² |  | 185 | 195 | 132 | 55 | [62 empty] | Total Load R: 378; Total Load Y: 367; Total Load B: 323; Total Load N: 180 | 378 | 323 | 27.498 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN1 | 23.220709, 56.51406 | 134 | Ground (GMT) | 3 | 1000 | 09/06/2026, 22:36 | 2 | 245 | 243 | 245 | 423 | 424 | 430 | 185 mm² |  | 8 | 5 | 7 | 6 | 185 mm² |  | 58 | 49 | 68 | 18 | 185 mm² |  | 84 | 48 | 68 | 33 | 185 mm² |  | 72 | 38 | 25 | 39 | 185 mm² |  | 154 | 206 | 197 | 32 | [62 empty] | Total Load R: 376; Total Load Y: 346; Total Load B: 365; Total Load N: 128 | 376 | 346 | 27.5479 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN1 | 23.22145, 56.515303 | 1391 | Ground (GMT) | 3 | 1000 | 05/06/2026, 13:57 | 1 | 251 | 250 | 254 | 434 | 439 | 438 | [12 empty] | 240 mm² |  | 21 | 46 | 41 | 17 | 240 mm² |  | 30 | 31 | 14 | 14 | [6 empty] | 185 mm² |  | 87 | 103 | 99 | 33 | [56 empty] | Total Load R: 138; Total Load Y: 180; Total Load B: 154; Total Load N: 64 | 180 | 138 | 13.5308 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 | 23.22145, 56.515303 | 1391 | Ground (GMT) | 4 | 1000 | 09/06/2026, 22:28 | 2 | 251 | 250 | 251 | 435 | 435 | 434 | [12 empty] | 240 mm² |  | 40 | 68 | 71 | 42 | 240 mm² |  | 63 | 28 | 69 | 38 | [6 empty] | 185 mm² |  | 85 | 120 | 124 | 32 | [56 empty] | Total Load R: 188; Total Load Y: 216; Total Load B: 264; Total Load N: 112 | 264 | 188 | 19.8909 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 | 23.222374, 56.514306 | 133 | Ground (GMT) | 3 | 1000 | 05/06/2026, 13:51 | 1 | 244 | 245 | 247 | 422 | 427 | 427 | [14 empty] | 18 | 57 | 50 | 25 | 120 mm² |  | 90 | 92 | 104 | 23 | 120 mm² |  | 210 | 143 | 108 | 110 | 120 mm² |  | 70 | 41 | 69 | 31 | 185 mm² |  | 44 | 58 | 18 | 37 | 185 mm² |  | 58 | 67 | 87 | 15 | [44 empty] | Total Load R: 490; Total Load Y: 458; Total Load B: 436; Total Load N: 241 | 490 | 436 | 35.8153 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN1 | 23.222374, 56.514306 | 133 | Ground (GMT) | 3 | 1000 | 09/06/2026, 22:20 | 2 | 244 | 243 | 245 | 421 | 425 | 423 | [12 empty] | 185 mm² |  | 22 | 25 | 42 | 17 | 120 mm² |  | 181 | 158 | 133 | 54 | 120 mm² |  | 114 | 146 | 69 | 85 | 120 mm² |  | 125 | 64 | 76 | 42 | 120 mm² |  | 35 | 29 | 15 | 17 | 185 mm² |  | 73 | 80 | 106 | 27 | [44 empty] | Total Load R: 550; Total Load Y: 502; Total Load B: 441; Total Load N: 242 | 550 | 441 | 40.1056 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 | 23.223631, 56.513116 | 132 | Pole (PMT) | 3 | 315 | 05/06/2026, 13:44 | 1 | 243 | 244 | 246 | 421 | 426 | 425 | 120 mm² |  | 71 | 76 | 29 | 55 | 185 mm² |  | 155 | 102 | 169 | 72 | [80 empty] | Total Load R: 226; Total Load Y: 178; Total Load B: 198; Total Load N: 127 | 226 | 178 | 52.3167 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 | 23.223631, 56.513116 | 132 | Pole (PMT) | 3 | 315 | 09/06/2026, 22:14 | 2 | 242 | 243 | 244 | 420 | 422 | 420 | 120 mm² |  | 58 | 73 | 53 | 21 | 185 mm² |  | 129 | 106 | 125 | 30 | [80 empty] | Total Load R: 187; Total Load Y: 179; Total Load B: 178; Total Load N: 51 | 187 | 178 | 43.1858 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN1 | 23.228394, 56.511028 | 1375 | Ground (GMT) | 3 | 1000 | 05/06/2026, 13:36 | 1 | 247 | 247 | 249 | 428 | 433 | 432 | [6 empty] | 185 mm² |  | 98 | 78 | 105 | 40 | 185 mm² |  | 67 | 60 | 102 | 41 | 185 mm² |  | 112 | 26 | 81 | 91 | [6 empty] | 185 mm² |  | 114 | 144 | 115 | 25 | [56 empty] | Total Load R: 391; Total Load Y: 308; Total Load B: 403; Total Load N: 197 | 403 | 308 | 29.8751 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN1 | 23.228394, 56.511028 | 1375 | Ground (GMT) | 3 | 1000 | 09/06/2026, 21:57 | 2 | 247 | 246 | 248 | 429 | 430 | 428 | [6 empty] | 185 mm² |  | 105 | 70 | 126 | 66 | 185 mm² |  | 29 | 57 | 63 | 35 | 185 mm² |  | 34 | 18 | 86 | 56 | [6 empty] | 185 mm² |  | 102 | 95 | 106 | 17 | [56 empty] | Total Load R: 270; Total Load Y: 240; Total Load B: 381; Total Load N: 174 | 381 | 240 | 28.3102 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 | 23.225175, 56.5111 | 1447 | Ground (GMT) |  | 1000 | 05/06/2026, 13:30 | 1 | 246 | 246 | 249 | 426 | 431 | 429 | 185 mm² | [5 empty] | 185 mm² |  | 93 | 79 | 46 | 47 | 185 mm² |  | 122 | 100 | 76 | 40 | 185 mm² |  | 87 | 66 | 62 | 29 | 185 mm² |  | 68 | 82 | 99 | 33 | 185 mm² |  | 32 | 82 | 26 | 54 | 185 mm² |  | 50 | 26 | 84 | 49 | 185 mm² |  | 46 | 125 | 62 | 64 | [44 empty] | Total Load R: 498; Total Load Y: 560; Total Load B: 455; Total Load N: 316 | 560 | 455 | 41.3198 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 | 23.225175, 56.5111 | 1447 | Ground (GMT) | 3 | 1000 | 09/06/2026, 22:06 | 2 | 245 | 244 | 246 | 424 | 425 | 424 | [6 empty] | 185 mm² |  | 81 | 31 | 24 | 53 | 185 mm² |  | 72 | 88 | 69 | 22 | 185 mm² |  | 71 | 64 | 111 | 39 | 185 mm² |  | 63 | 76 | 42 | 20 | 185 mm² |  | 44 | 58 | 60 | 24 | 185 mm² |  | 58 | 48 | 56 | 25 | 185 mm² |  | 40 | 71 | 44 | 24 | [44 empty] | Total Load R: 429; Total Load Y: 436; Total Load B: 406; Total Load N: 207 | 436 | 406 | 32.0194 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN3 | 23.223338, 56.558491 | 4670 | Pole (PMT) |  | 100 | 29/05/2026, 15:37 | 1 | 244 | 243 | 245 | 422 | 425 | 424 | 185 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN3 | 23.223338, 56.558491 | 4670 | Pole (PMT) | 3 | 100 | 10/06/2026, 22:00 | 2 | 250 | 248 | 251 | 432 | 435 | 433 | 185 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN3 | 23.220429, 56.55207 | 4254 | Pole (PMT) |  | 315 | 29/05/2026, 15:31 | 1 | 244 | 243 | 246 | 422 | 426 | 425 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN3 | 23.220429, 56.55207 | 4254 | Pole (PMT) | 3 | 315 | 10/06/2026, 21:57 | 2 | 250 | 249 | 252 | 432 | 437 | 434 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN3 | 23.22164, 56.546782 | 4646 | Pole (PMT) |  | 100 | 29/05/2026, 15:27 | 1 | 242 | 242 | 244 | 417 | 426 | 421 | 185 mm² |  | 24 | 9 | 1 | 13 | [86 empty] | Total Load R: 24; Total Load Y: 9; Total Load B: 1; Total Load N: 13 | 24 | 1 | 17.3344 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.22164, 56.546782 | 4646 | Pole (PMT) | 3 | 100 | 10/06/2026, 21:47 | 2 | 249 | 249 | 251 | 431 | 436 | 433 | 185 mm² |  | 13 | 0 | 0 | 9 | [86 empty] | Total Load R: 13; Total Load Y: 0; Total Load B: 0; Total Load N: 9 | 13 | 0 | 9.7047 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.223816, 56.541588 | 1947 | Pole (PMT) |  | 315 | 29/05/2026, 15:22 | 1 | 243 | 245 | 243 | 423 | 421 | 426 | 185 mm² |  | 41 | 24 | 46 | 21 | 185 mm² |  | 0 | 1 | 0 | 1 | [80 empty] | Total Load R: 41; Total Load Y: 25; Total Load B: 46; Total Load N: 22 | 46 | 25 | 10.6991 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.223816, 56.541588 | 1947 | Pole (PMT) | 3 | 315 | 10/06/2026, 21:42 | 2 | 250 | 252 | 251 | 435 | 435 | 435 | 185 mm² |  | 3 | 15 | 13 | 10 | 185 mm² |  | 0 | 15 | 0 | 15 | [80 empty] | Total Load R: 3; Total Load Y: 30; Total Load B: 13; Total Load N: 25 | 30 | 3 | 7.1756 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.218417, 56.543408 | 1857 | Ground (GMT) |  | 500 | 29/05/2026, 15:15 | 1 | 244 | 245 | 243 | 424 | 422 | 425 | 185 mm² |  | 24 | 30 | 52 | 27 | 185 mm² |  | 0 | 0 | 0 | 0 | 240 mm² |  | 0 | 0 | 0 | 0 | [74 empty] | Total Load R: 24; Total Load Y: 30; Total Load B: 52; Total Load N: 27 | 52 | 24 | 7.6377 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.218417, 56.543408 | 1857 | Ground (GMT) | 3 | 500 | 10/06/2026, 21:37 | 2 | 249 | 251 | 250 | 434 | 433 | 435 | 185 mm² |  | 52 | 20 | 56 | 26 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | [74 empty] | Total Load R: 52; Total Load Y: 20; Total Load B: 56; Total Load N: 26 | 56 | 20 | 8.4192 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.214696, 56.541149 | 337 | Ground (GMT) |  | 1000 | 29/05/2026, 15:08 | 1 | 242 | 241 | 244 | 420 | 423 | 421 | 185 mm² |  | 67 | 54 | 77 | 15 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 45 | 47 | 56 | 13 | 185 mm² |  | 26 | 0 | 13 | 16 | 185 mm² |  | 74 | 114 | 106 | 63 | 185 mm² |  | 18 | 13 | 20 | 14 | [56 empty] | Total Load R: 230; Total Load Y: 228; Total Load B: 272; Total Load N: 121 | 272 | 228 | 19.7869 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.214696, 56.541149 | 337 | Ground (GMT) | 3 | 1000 | 10/06/2026, 21:30 | 2 | 249 | 248 | 251 | 431 | 434 | 432 | 185 mm² |  | 34 | 36 | 22 | 13 | 185 mm² |  | 8 | 7 | 7 | 3 | 185 mm² |  | 17 | 47 | 3 | 23 | 185 mm² |  | 16 | 0 | 12 | 7 | 185 mm² |  | 57 | 29 | 43 | 27 | 185 mm² |  | 21 | 4 | 53 | 61 | [56 empty] | Total Load R: 153; Total Load Y: 123; Total Load B: 140; Total Load N: 134 | 153 | 123 | 11.4217 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN3 | 23.216047, 56.541191 | 4538 | Ground (GMT) |  | 1000 | 10/06/2026, 21:22 | 1 | 242 | 245 | 244 | 424 | 421 | 426 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | [62 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN3 | 23.216047, 56.541191 | 4538 | Ground (GMT) |  | 1000 | 10/06/2026, 21:25 | 2 | 248 | 251 | 249 | 433 | 429 | 434 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | [62 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN5 | 23.21457, 56.519268 | 116 | Ground (GMT) |  | 1000 | 29/05/2026, 14:50 | 1 | 247 | 247 | 243 | 430 | 423 | 425 | 185 mm² |  | 75 | 40 | 98 | 28 | 185 mm² |  | 82 | 30 | 102 | 57 | 185 mm² |  | 102 | 92 | 91 | 20 | 185 mm² |  | 43 | 29 | 16 | 15 | 240 mm² |  | 138 | 148 | 259 | 106 | 185 mm² |  | 77 | 118 | 128 | 53 | [56 empty] | Total Load R: 517; Total Load Y: 457; Total Load B: 694; Total Load N: 279 | 694 | 457 | 51.6879 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN5 | 23.21457, 56.519268 | 116 | Ground (GMT) | 3 | 1000 | 09/06/2026, 22:57 | 2 | 247 | 247 | 245 | 429 | 428 | 427 | 185 mm² |  | 39 | 59 | 32 | 31 | 185 mm² |  | 119 | 56 | 70 | 30 | 185 mm² |  | 101 | 63 | 75 | 10 | 185 mm² |  | 0 | 63 | 3 | 40 | 240 mm² |  | 131 | 123 | 164 | 40 | 185 mm² |  | 75 | 129 | 108 | 46 | [56 empty] | Total Load R: 465; Total Load Y: 493; Total Load B: 452; Total Load N: 197 | 493 | 452 | 36.6324 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN5 | 23.210917, 56.523702 | 122 | Pole (PMT) |  | 50 | 29/05/2026, 14:42 | 1 | 242 | 245 | 243 | 421 | 420 | 421 | 185 mm² |  | 13 | 2 | 0 | 13 | [86 empty] | Total Load R: 13; Total Load Y: 2; Total Load B: 0; Total Load N: 13 | 13 | 0 | 18.959 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN5 | 23.210917, 56.523702 | 122 | Pole (PMT) | 3 | 50 | 09/06/2026, 22:49 | 2 | 240 | 243 | 245 | 417 | 412 | 425 | 185 mm² |  | 48 | 18 | 3 | 37 | [86 empty] | Total Load R: 48; Total Load Y: 18; Total Load B: 3; Total Load N: 37 | 48 | 3 | 69.3375 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN5 | 23.212913, 56.523714 | 121 | Ground (GMT) |  | 1000 | 29/05/2026, 14:36 | 1 | 241 | 243 | 242 | 420 | 418 | 422 | [6 empty] | 185 mm² |  | 63 | 43 | 27 | 30 | 185 mm² |  | 160 | 138 | 114 | 36 | 185 mm² |  | 27 | 26 | 11 | 23 | 185 mm² |  | 26 | 61 | 21 | 39 | 185 mm² |  | 121 | 205 | 190 | 58 | [56 empty] | Total Load R: 397; Total Load Y: 473; Total Load B: 363; Total Load N: 186 | 473 | 363 | 34.4089 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN5 | 23.212913, 56.523714 | 121 | Ground (GMT) | 3 | 1000 | 09/06/2026, 22:44 | 2 | 243 | 244 | 244 | 422 | 422 | 424 | [6 empty] | 185 mm² |  | 67 | 68 | 41 | 34 | 185 mm² |  | 72 | 65 | 74 | 22 | 185 mm² |  | 58 | 34 | 24 | 32 | 185 mm² |  | 33 | 91 | 39 | 52 | 185 mm² |  | 76 | 113 | 124 | 29 | [56 empty] | Total Load R: 306; Total Load Y: 371; Total Load B: 302; Total Load N: 169 | 371 | 302 | 27.1173 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN5 | 23.213929, 56.52234 | 4507 | Ground (GMT) |  | 500 | 29/05/2026, 14:28 | 1 | 243 | 242 | 244 | 419 | 421 | 421 | 185 mm² |  | 44 | 49 | 59 | 27 | 185 mm² |  | 36 | 50 | 26 | 20 | 185 mm² |  | 50 | 49 | 32 | 28 | [74 empty] | Total Load R: 130; Total Load Y: 148; Total Load B: 117; Total Load N: 75 | 148 | 117 | 21.4816 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN5 | 23.213929, 56.52234 | 4507 | Ground (GMT) | 3 | 500 | 09/06/2026, 22:36 | 2 | 244 | 243 | 244 | 422 | 424 | 423 | 185 mm² |  | 54 | 62 | 81 | 25 | 185 mm² |  | 29 | 32 | 27 | 8 | 185 mm² |  | 83 | 71 | 59 | 45 | [74 empty] | Total Load R: 166; Total Load Y: 165; Total Load B: 167; Total Load N: 78 | 167 | 165 | 24.4129 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN5 | 23.215237, 56.521137 | 117 | Ground (GMT) |  | 1000 | 29/05/2026, 14:22 | 1 | 243 | 243 | 245 | 419 | 424 | 424 | 185 mm² |  | 159 | 80 | 97 | 30 | 185 mm² |  | 63 | 49 | 83 | 34 | 120 mm² |  | 133 | 101 | 85 | 34 | 185 mm² |  | 60 | 10 | 43 | 60 | 185 mm² |  | 40 | 88 | 125 | 47 | [6 empty] | 120 mm² |  | 2 | 0 | 0 | 2 | [50 empty] | Total Load R: 457; Total Load Y: 328; Total Load B: 433; Total Load N: 207 | 457 | 328 | 33.1658 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN5 | 23.215237, 56.521137 | 117 | Ground (GMT) | 3 | 1000 | 09/06/2026, 22:32 | 2 | 243 | 243 | 244 | 421 | 423 | 422 | 185 mm² |  | 124 | 43 | 74 | 20 | 185 mm² |  | 53 | 27 | 45 | 27 | 120 mm² |  | 87 | 104 | 86 | 27 | 185 mm² |  | 25 | 60 | 68 | 25 | 185 mm² |  | 35 | 32 | 82 | 58 | [6 empty] | 120 mm² |  | 11 | 0 | 1 | 10 | [50 empty] | Total Load R: 335; Total Load Y: 266; Total Load B: 356; Total Load N: 167 | 356 | 266 | 25.9593 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN5 | 23.216665, 56.521443 | 118 | Ground (GMT) |  | 1000 | 29/05/2026, 14:15 | 1 | 245 | 243 | 242 | 424 | 421 | 419 | [24 empty] | 185 mm² |  | 96 | 127 | 99 | 17 | 185 mm² |  | 131 | 161 | 148 | 21 | 120 mm² |  | 137 | 131 | 93 | 55 | 185 mm² |  | 61 | 39 | 105 | 52 | [44 empty] | Total Load R: 425; Total Load Y: 458; Total Load B: 445; Total Load N: 145 | 458 | 425 | 33.635 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN5 | 23.216665, 56.521443 | 118 | Ground (GMT) | 3 | 1000 | 09/06/2026, 22:23 | 2 | 244 | 243 | 243 | 424 | 423 | 422 | [24 empty] | 185 mm² |  | 74 | 99 | 60 | 15 | 185 mm² |  | 86 | 75 | 122 | 46 | 120 mm² |  | 89 | 99 | 98 | 29 | 185 mm² |  | 123 | 125 | 11 | 24 | [44 empty] | Total Load R: 372; Total Load Y: 398; Total Load B: 291; Total Load N: 114 | 398 | 291 | 29.2287 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN8 | 23.21649, 56.516316 | 115 | Ground (GMT) |  | 1000 | 10/06/2026, 21:06 | 1 | 245 | 245 | 246 | 423 | 428 | 426 | 185 mm² |  | 63 | 43 | 36 | 20 | 185 mm² |  | 65 | 18 | 28 | 46 | 185 mm² |  | 139 | 56 | 108 | 71 | 185 mm² |  | 38 | 62 | 130 | 70 | 185 mm² |  | 3 | 17 | 15 | 12 | 185 mm² |  | 1 | 1 | 0 | 1 | [56 empty] | Total Load R: 309; Total Load Y: 197; Total Load B: 317; Total Load N: 220 | 317 | 197 | 23.2252 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN8 | 23.21649, 56.516316 | 115 | Ground (GMT) | 3 | 1000 | 10/06/2026, 21:10 | 2 | 246 | 246 | 248 | 423 | 431 | 428 | 185 mm² |  | 85 | 26 | 3 | 62 | 185 mm² |  | 98 | 72 | 25 | 68 | 185 mm² |  | 134 | 124 | 159 | 54 | 185 mm² |  | 54 | 9 | 78 | 83 | 185 mm² |  | 44 | 49 | 28 | 30 | 185 mm² |  | 58 | 24 | 20 | 33 | [56 empty] | Total Load R: 473; Total Load Y: 304; Total Load B: 313; Total Load N: 330 | 473 | 304 | 34.6547 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN8 | 23.219057, 56.516703 | 123 | Ground (GMT) |  | 2000 | 29/05/2026, 13:58 | 1 | 246 | 246 | 248 | 425 | 430 | 406 | 240 mm² |  | 14 | 2 | 2 | 12 | 240 mm² |  | 1 | 0 | 0 | 0 | [36 empty] | 185 mm² |  | 19 | 14 | 44 | 22 | 185 mm² |  | 17 | 12 | 41 | 20 | 240 mm² |  | 15 | 12 | 0 | 17 | 240 mm² |  | 15 | 2 | 23 | 14 | 240 mm² |  | 0 | 35 | 50 | 33 | 240 mm² |  | 29 | 10 | 18 | 15 | [6 empty] | 240 mm² |  | 27 | 32 | 9 | 16 | 137 | 119 | 187 | 149 | 187 | 119 | 6.8827 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN8 | 23.219057, 56.516703 | 123 | Ground (GMT) | 3 | 2000 | 10/06/2026, 21:05 | 2 | 248 | 247 | 249 | 428 | 431 | 430 | 185 mm² |  | 18 | 22 | 47 | 29 | 185 mm² |  | 16 | 18 | 35 | 13 | 240 mm² |  | 4 | 19 | 15 | 14 | 240 mm² |  | 32 | 26 | 46 | 32 | 240 mm² |  | 5 | 4 | 82 | 69 | 185 mm² |  | 14 | 10 | 13 | 3 | [6 empty] | 185 mm² |  | 44 | 0 | 1 | 17 | 240 mm² |  | 14 | 2 | 2 | 9 | 240 mm² |  | 1 | 0 | 0 | 1 | [32 empty] | Total Load R: 148; Total Load Y: 101; Total Load B: 241; Total Load N: 187 | 241 | 101 | 8.9329 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN8 | 23.220092, 56.516563 | 124 | Ground (GMT) |  | 1000 | 29/05/2026, 13:47 | 1 | 245 | 245 | 247 | 424 | 427 | 429 | 185 mm² |  | 28 | 48 | 34 | 19 | 185 mm² |  | 74 | 21 | 63 | 58 | [6 empty] | 120 mm² |  | 71 | 56 | 122 | 53 | 120 mm² |  | 182 | 183 | 174 | 29 | 185 mm² |  | 14 | 11 | 16 | 6 | 185 mm² |  | 9 | 33 | 54 | 36 | [50 empty] | Total Load R: 378; Total Load Y: 352; Total Load B: 463; Total Load N: 201 | 463 | 352 | 34.0022 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN8 | 23.220092, 56.516563 | 124 | Ground (GMT) | 3 | 1000 | 10/06/2026, 20:58 | 2 | 246 | 246 | 248 | 426 | 430 | 428 | 185 mm² |  | 112 | 58 | 77 | 57 | 185 mm² |  | 80 | 60 | 80 | 27 | [6 empty] | 120 mm² |  | 78 | 49 | 71 | 20 | 120 mm² |  | 99 | 77 | 110 | 49 | 240 mm² |  | 0 | 3 | 3 | 3 | 185 mm² |  | 39 | 36 | 20 | 15 | [50 empty] | Total Load R: 408; Total Load Y: 283; Total Load B: 361; Total Load N: 171 | 408 | 283 | 30.1044 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN8 | 23.223507, 56.516475 | 125 | Ground (GMT) |  | 1000 | 29/05/2026, 13:42 | 1 | 246 | 246 | 248 | 424 | 430 | 428 | [18 empty] | 120 mm² |  | 74 | 42 | 61 | 31 | 120 mm² |  | 134 | 66 | 87 | 63 | 185 mm² |  | 0 | 0 | 0 | 0 | 240 mm² |  | 4 | 15 | 1 | 10 | 185 mm² |  | 0 | 2 | 1 | 1 | [44 empty] | Total Load R: 212; Total Load Y: 125; Total Load B: 150; Total Load N: 105 | 212 | 125 | 15.5691 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN8 | 23.223507, 56.516475 | 125 | Ground (GMT) | 3 | 1000 | 10/06/2026, 20:52 | 2 | 247 | 248 | 247 | 438 | 430 | 433 | [18 empty] | 120 mm² |  | 35 | 25 | 34 | 18 | 120 mm² |  | 375 | 200 | 309 | 141 | 120 mm² |  | 0 | 0 | 0 | 0 | 240 mm² |  | 2 | 5 | 14 | 11 | 240 mm² |  | 10 | 1 | 5 | 4 | [44 empty] | Total Load R: 422; Total Load Y: 231; Total Load B: 362; Total Load N: 174 | 422 | 231 | 32.0145 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN8 | 23.224835, 56.515428 | 1408 | Ground (GMT) |  | 2000 | 29/05/2026, 13:35 | 1 | 245 | 245 | 248 | 424 | 429 | 429 | [30 empty] | 240 mm² |  | 77 | 87 | 97 | 20 | 240 mm² |  | 51 | 64 | 67 | 11 | 240 mm² |  | 32 | 24 | 30 | 8 | [12 empty] | 185 mm² |  | 23 | 64 | 5 | 67 | 185 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 52 | 23 | 26 | 24 | 185 mm² |  | 0 | 14 | 1 | 10 | 185 mm² |  | 51 | 12 | 8 | 42 |  |  | Total Load R: 286; Total Load Y: 288; Total Load B: 234; Total Load N: 182 | 288 | 234 | 10.5752 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN8 | 23.224835, 56.515428 | 1408 | Ground (GMT) | 3 | 2000 | 10/06/2026, 20:47 | 2 | 247 | 247 | 249 | 426 | 431 | 430 | [30 empty] | 240 mm² |  | 129 | 98 | 134 | 54 | 240 mm² |  | 24 | 21 | 21 | 11 | 240 mm² |  | 61 | 83 | 65 | 29 | [12 empty] | 185 mm² |  | 37 | 24 | 25 | 21 | 185 mm² |  | 23 | 8 | 1 | 12 | 120 mm² |  | 32 | 13 | 13 | 20 | 185 mm² |  | 1 | 28 | 1 | 25 | 185 mm² |  | 64 | 17 | 25 | 34 |  |  | Total Load R: 371; Total Load Y: 292; Total Load B: 285; Total Load N: 206 | 371 | 285 | 13.6872 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN8 | 23.22585, 56.517291 | 127 | Ground (GMT) |  | 1000 | 29/05/2026, 15:53 | 1 | 244 | 244 | 246 | 421 | 426 | 426 | [12 empty] | 240 mm² |  | 55 | 64 | 70 | 14 | 240 mm² |  | 107 | 108 | 66 | 35 | 240 mm² |  | 134 | 135 | 127 | 44 | 240 mm² |  | 18 | 20 | 54 | 35 | 240 mm² |  | 74 | 56 | 95 | 30 | 240 mm² |  | 77 | 85 | 84 | 19 | [44 empty] | Total Load R: 465; Total Load Y: 468; Total Load B: 496; Total Load N: 177 | 496 | 465 | 36.168 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN8 | 23.22585, 56.517291 | 127 | Ground (GMT) | 3 | 1000 | 10/06/2026, 20:39 | 2 | 246 | 245 | 247 | 424 | 428 | 427 | [12 empty] | 240 mm² |  | 33 | 80 | 68 | 40 | 240 mm² |  | 143 | 132 | 83 | 46 | 240 mm² |  | 92 | 143 | 186 | 55 | 240 mm² |  | 30 | 45 | 45 | 29 | 240 mm² |  | 74 | 23 | 129 | 94 | 240 mm² |  | 65 | 82 | 64 | 16 | [44 empty] | Total Load R: 437; Total Load Y: 505; Total Load B: 575; Total Load N: 280 | 575 | 437 | 42.2274 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN8 | 23.227558, 56.515208 | 126 | Ground (GMT) |  | 1000 | 29/05/2026, 15:49 | 1 | 244 | 244 | 247 | 423 | 428 | 426 | [12 empty] | 185 mm² |  | 70 | 80 | 97 | 21 | 120 mm² |  | 64 | 95 | 80 | 23 | 120 mm² |  | 170 | 110 | 96 | 63 | 120 mm² |  | 80 | 52 | 38 | 45 | 185 mm² |  | 50 | 77 | 75 | 29 | 185 mm² |  | 19 | 42 | 13 | 27 | [44 empty] | Total Load R: 453; Total Load Y: 456; Total Load B: 399; Total Load N: 208 | 456 | 399 | 33.4092 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN8 | 23.227558, 56.515208 | 126 | Ground (GMT) | 3 | 1000 | 10/06/2026, 20:33 | 2 | 246 | 245 | 248 | 426 | 429 | 426 | [12 empty] | 185 mm² |  | 59 | 56 | 48 | 16 | 120 mm² |  | 56 | 75 | 26 | 43 | 120 mm² |  | 35 | 71 | 77 | 38 | 120 mm² |  | 109 | 104 | 79 | 47 | 185 mm² |  | 39 | 91 | 70 | 53 | 185 mm² |  | 35 | 70 | 67 | 18 | [44 empty] | Total Load R: 333; Total Load Y: 467; Total Load B: 367; Total Load N: 215 | 467 | 333 | 34.4578 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN8 | 23.228146, 56.517132 | 128 | Ground (GMT) |  | 1000 | 29/05/2026, 13:07 | 1 | 247 | 246 | 250 | 426 | 432 | 429 | 185 mm² |  | 53 | 58 | 34 | 27 | 185 mm² |  | 33 | 108 | 57 | 33 | 185 mm² |  | 87 | 107 | 72 | 40 | [74 empty] | Total Load R: 173; Total Load Y: 273; Total Load B: 163; Total Load N: 100 | 273 | 163 | 20.1434 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN8 | 23.228146, 56.517132 | 128 | Ground (GMT) | 3 | 1000 | 10/06/2026, 20:25 | 2 | 248 | 247 | 250 | 428 | 433 | 430 | 185 mm² |  | 50 | 60 | 19 | 30 | 185 mm² |  | 61 | 34 | 33 | 26 | 185 mm² |  | 93 | 106 | 41 | 60 | [74 empty] | Total Load R: 204; Total Load Y: 200; Total Load B: 93; Total Load N: 116 | 204 | 93 | 15.1229 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN8 | 23.229456, 56.515532 | 2288 | Ground (GMT) |  | 1000 | 29/05/2026, 12:59 | 1 | 248 | 247 | 250 | 427 | 433 | 431 | 185 mm² |  | 27 | 63 | 53 | 24 | 185 mm² |  | 53 | 53 | 41 | 20 | 185 mm² |  | 44 | 33 | 39 | 15 | 185 mm² |  | 68 | 40 | 54 | 28 | [68 empty] | Total Load R: 192; Total Load Y: 189; Total Load B: 187; Total Load N: 87 | 192 | 187 | 14.2 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN8 | 23.229456, 56.515532 | 2288 | Ground (GMT) | 3 | 1000 | 10/06/2026, 20:21 | 2 | 248 | 247 | 250 | 428 | 434 | 430 | 185 mm² |  | 19 | 32 | 10 | 24 | 185 mm² |  | 35 | 6 | 29 | 33 | 185 mm² |  | 20 | 89 | 37 | 53 | 185 mm² |  | 161 | 53 | 69 | 87 | [68 empty] | Total Load R: 235; Total Load Y: 180; Total Load B: 145; Total Load N: 197 | 235 | 145 | 17.421 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN6 | 23.222014, 56.51988 | 2189 | Pole (PMT) |  | 315 | 28/05/2026, 15:33 | 1 | 243 | 242 | 244 | 419 | 423 | 422 | 185 mm² |  | 67 | 71 | 98 | 35 | [86 empty] | Total Load R: 67; Total Load Y: 71; Total Load B: 98; Total Load N: 35 | 98 | 67 | 22.5782 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN6 | 23.222014, 56.51988 | 2189 | Pole (PMT) | 3 | 315 | 09/06/2026, 22:15 | 2 | 248 | 247 | 248 | 429 | 430 | 430 | 185 mm² |  | 12 | 5 | 40 | 27 | [86 empty] | Total Load R: 12; Total Load Y: 5; Total Load B: 40; Total Load N: 27 | 40 | 5 | 9.4356 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN6 | 23.222845, 56.519081 | 285 | Pole (PMT) |  | 315 | 28/05/2026, 15:29 | 1 | 244 | 242 | 244 | 420 | 426 | 422 | 120 mm² |  | 64 | 92 | 79 | 13 | 120 mm² |  | 0 | 9 | 2 | 8 | [80 empty] | Total Load R: 64; Total Load Y: 101; Total Load B: 81; Total Load N: 21 | 101 | 64 | 23.325 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN6 | 23.222845, 56.519081 | 285 | Pole (PMT) | 3 | 315 | 09/06/2026, 22:10 | 2 | 247 | 245 | 247 | 428 | 429 | 427 | 120 mm² |  | 15 | 69 | 69 | 16 | 120 mm² |  | 10 | 0 | 1 | 9 | [80 empty] | Total Load R: 25; Total Load Y: 69; Total Load B: 70; Total Load N: 25 | 70 | 25 | 16.4737 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN6 | 23.22508, 56.523125 | 284 | Pole (PMT) |  | 315 | 28/05/2026, 15:24 | 1 | 240 | 240 | 243 | 413 | 421 | 418 | 185 mm² |  | 182 | 116 | 122 | 58 | 185 mm² |  | 91 | 89 | 63 | 21 | [80 empty] | Total Load R: 273; Total Load Y: 205; Total Load B: 185; Total Load N: 79 | 273 | 185 | 61.9959 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN6 | 23.22508, 56.523125 | 284 | Pole (PMT) | 3 | 315 | 09/06/2026, 22:06 | 2 | 243 | 244 | 246 | 419 | 421 | 426 | 185 mm² |  | 146 | 85 | 72 | 69 | 185 mm² |  | 125 | 48 | 56 | 74 | [80 empty] | Total Load R: 271; Total Load Y: 133; Total Load B: 128; Total Load N: 143 | 271 | 128 | 62.4358 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN4 |  | 1684 | Ground (GMT) |  | 1000 | 28/05/2026, 15:08 | 1 | 243 | 241 | 244 | 419 | 421 | 420 | 120 mm² |  | 24 | 11 | 70 | 55 | 185 mm² |  | 62 | 42 | 79 | 15 | 185 mm² |  | 85 | 91 | 140 | 56 | 185 mm² |  | 13 | 16 | 27 | 23 | [68 empty] | Total Load R: 184; Total Load Y: 160; Total Load B: 316; Total Load N: 149 | 316 | 160 | 22.933 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN4 |  | 1684 | Ground (GMT) | 3 | 1000 | 09/06/2026, 21:49 | 2 | 248 | 246 | 248 | 427 | 431 | 429 | 120 mm² |  | 28 | 7 | 54 | 46 | 185 mm² |  | 4 | 37 | 22 | 28 | 185 mm² |  | 91 | 108 | 112 | 50 | 185 mm² |  | 124 | 92 | 73 | 44 | [68 empty] | Total Load R: 247; Total Load Y: 244; Total Load B: 261; Total Load N: 168 | 261 | 244 | 19.3032 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN6 | 23.22965, 56.522146 | 1444 | Ground (GMT) |  | 500 | 09/06/2026, 21:40 | 1 | 244 | 242 | 246 | 422 | 426 | 424 | 50 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN6 | 23.22965, 56.522146 | 1444 | Ground (GMT) | 3 | 500 | 09/06/2026, 21:40 | 2 | 249 | 247 | 250 | 431 | 435 | 432 | 50 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN4 |  | 130 | Ground (GMT) |  | 1000 | 28/05/2026, 14:59 | 1 | 249 | 247 | 245 | 428 | 433 | 418 | [12 empty] | 120 mm² |  | 70 | 74 | 46 | 26 | [6 empty] | 120 mm² |  | 85 | 74 | 85 | 17 | 120 mm² |  | 100 | 49 | 128 | 56 | 120 mm² |  | 2 | 64 | 33 | 56 | 240 mm² |  | 13 | 10 | 28 | 27 | [44 empty] | Total Load R: 270; Total Load Y: 271; Total Load B: 320; Total Load N: 182 | 320 | 270 | 23.7222 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN4 |  | 130 | Ground (GMT) | 3 | 1000 | 09/06/2026, 21:42 | 2 | 254 | 253 | 242 | 439 | 440 | 439 | [12 empty] | 120 mm² |  | 14 | 30 | 39 | 26 | [6 empty] | 120 mm² |  | 98 | 57 | 56 | 16 | 120 mm² |  | 42 | 52 | 85 | 31 | 120 mm² |  | 5 | 43 | 61 | 49 | 240 mm² |  | 15 | 26 | 10 | 18 | [44 empty] | Total Load R: 174; Total Load Y: 208; Total Load B: 251; Total Load N: 140 | 251 | 174 | 19.0853 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN4 | 23.236046, 56.516329 | 925 | Ground (GMT) |  | 1000 | 28/05/2026, 14:55 | 1 | 239 | 242 | 243 | 417 | 416 | 421 | 185 mm² |  | 143 | 57 | 38 | 35 | 185 mm² |  | 144 | 19 | 142 | 92 | 185 mm² |  | 150 | 136 | 99 | 23 | 185 mm² |  | 27 | 43 | 40 | 13 | 185 mm² |  | 177 | 118 | 143 | 25 | [6 empty] | 185 mm² |  | 66 | 46 | 78 | 27 | [50 empty] | Total Load R: 707; Total Load Y: 419; Total Load B: 540; Total Load N: 215 | 707 | 419 | 51.0641 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN4 | 23.236046, 56.516329 | 925 | Ground (GMT) | 3 | 1000 | 09/06/2026, 21:34 | 2 | 246 | 247 | 249 | 427 | 426 | 432 | 185 mm² |  | 108 | 38 | 41 | 45 | 185 mm² |  | 107 | 54 | 64 | 46 | 185 mm² |  | 63 | 72 | 76 | 30 | 185 mm² |  | 23 | 55 | 22 | 32 | 185 mm² |  | 128 | 106 | 57 | 76 | [6 empty] | 185 mm² |  | 72 | 7 | 61 | 53 | [50 empty] | Total Load R: 501; Total Load Y: 332; Total Load B: 321; Total Load N: 282 | 501 | 321 | 37.0532 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN4 |  | 932 | Ground (GMT) |  | 1000 | 28/05/2026, 14:48 | 1 | 241 | 240 | 241 | 414 | 421 | 418 | 240 mm² |  | 95 | 64 | 52 | 24 | 185 mm² |  | 92 | 62 | 76 | 21 | 185 mm² |  | 131 | 189 | 14 | 64 | [6 empty] | 185 mm² |  | 3 | 31 | 24 | 39 | 185 mm² |  | 62 | 31 | 84 | 38 | 70 mm² |  | 0 | 0 | 0 | 0 | 70 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 383; Total Load Y: 377; Total Load B: 250; Total Load N: 186 | 383 | 250 | 27.4637 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN4 |  | 932 | Ground (GMT) | 3 | 1000 | 09/06/2026, 21:33 | 2 | 246 | 246 | 248 | 423 | 430 | 427 | 240 mm² |  | 80 | 84 | 56 | 25 | 185 mm² |  | 54 | 61 | 58 | 17 | 185 mm² |  | 180 | 340 | 148 | 169 | [6 empty] | 185 mm² |  | 30 | 40 | 10 | 25 | 185 mm² |  | 90 | 50 | 114 | 33 | 70 mm² |  | 0 | 0 | 0 | 0 | 70 mm² |  | 10 | 18 | 13 | 7 | [44 empty] | Total Load R: 444; Total Load Y: 593; Total Load B: 399; Total Load N: 276 | 593 | 399 | 43.4466 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN4 |  | 930 | Ground (GMT) |  | 1000 | 28/05/2026, 14:40 | 1 | 243 | 242 | 245 | 420 | 424 | 422 | 185 mm² |  | 76 | 161 | 89 | 70 | 240 mm² |  | 42 | 3 | 20 | 11 | 240 mm² |  | 15 | 21 | 32 | 18 | 240 mm² |  | 15 | 18 | 12 | 8 | [68 empty] | Total Load R: 148; Total Load Y: 203; Total Load B: 153; Total Load N: 107 | 203 | 148 | 14.7675 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN4 |  | 930 | Ground (GMT) | 3 | 1000 | 09/06/2026, 21:26 | 2 | 248 | 247 | 248 | 428 | 432 | 431 | 185 mm² |  | 62 | 45 | 98 | 52 | 240 mm² |  | 28 | 28 | 3 | 27 | 240 mm² |  | 51 | 45 | 51 | 18 | 240 mm² |  | 72 | 31 | 63 | 49 | [68 empty] | Total Load R: 213; Total Load Y: 149; Total Load B: 215; Total Load N: 146 | 215 | 149 | 15.9383 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN4 | 23.235023, 56.515596 | 926 | Ground (GMT) |  | 1000 | 09/06/2026, 21:28 | 1 | 241 | 243 | 245 | 418 | 420 | 424 | 120 mm² |  | 182 | 136 | 121 | 20 | 120 mm² |  | 45 | 12 | 16 | 23 | 185 mm² |  | 27 | 56 | 25 | 21 | 120 mm² |  | 53 | 43 | 124 | 56 | 185 mm² |  | 64 | 22 | 19 | 49 | 185 mm² |  | 63 | 28 | 10 | 61 | 70 mm² |  | 0 | 2 | 0 | 0 | [50 empty] | Total Load R: 434; Total Load Y: 299; Total Load B: 315; Total Load N: 230 | 434 | 299 | 31.4215 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN4 | 23.235023, 56.515596 | 926 | Ground (GMT) | 3 | 1000 | 09/06/2026, 21:28 | 2 | 246 | 248 | 249 | 429 | 427 | 433 | 120 mm² |  | 11 | 15 | 48 | 54 | 120 mm² |  | 50 | 27 | 30 | 19 | 185 mm² |  | 17 | 27 | 9 | 15 | 120 mm² |  | 18 | 42 | 52 | 40 | 185 mm² |  | 58 | 32 | 35 | 18 | 185 mm² |  | 110 | 42 | 36 | 63 | 70 mm² |  | 48 | 25 | 27 | 23 | [50 empty] | Total Load R: 312; Total Load Y: 210; Total Load B: 237; Total Load N: 232 | 312 | 210 | 23.1832 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 |  | 269 | Pole (PMT) |  | 315 | 28/05/2026, 14:30 | 1 | 245 | 243 | 242 | 424 | 422 | 418 | 120 mm² |  | 128 | 103 | 115 | 28 | [86 empty] | Total Load R: 128; Total Load Y: 103; Total Load B: 115; Total Load N: 28 | 128 | 103 | 29.8419 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 |  | 269 | Pole (PMT) | 3 | 315 | 09/06/2026, 21:13 | 2 | 250 | 249 | 248 | 433 | 430 | 432 | 120 mm² |  | 65 | 44 | 71 | 22 | [86 empty] | Total Load R: 65; Total Load Y: 44; Total Load B: 71; Total Load N: 22 | 71 | 44 | 16.9043 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN4 | 23.233952, 56.517279 | 16 | Ground (GMT) |  | 1000 | 28/05/2026, 14:28 | 1 | 242 | 242 | 245 | 417 | 421 | 424 | [6 empty] | 120 mm² |  | 105 | 68 | 51 | 23 | 185 mm² |  | 111 | 73 | 29 | 47 | 120 mm² |  | 22 | 33 | 43 | 15 | [6 empty] | 120 mm² |  | 149 | 202 | 148 | 31 | 185 mm² |  | 62 | 116 | 46 | 47 | [50 empty] | Total Load R: 449; Total Load Y: 492; Total Load B: 317; Total Load N: 163 | 492 | 317 | 35.5354 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN4 | 23.233952, 56.517279 | 16 | Ground (GMT) | 3 | 1000 | 09/06/2026, 21:20 | 2 | 246 | 248 | 249 | 429 | 428 | 433 | [6 empty] | 120 mm² |  | 155 | 71 | 80 | 22 | 185 mm² |  | 64 | 73 | 41 | 15 | 120 mm² |  | 44 | 31 | 40 | 14 | [6 empty] | 120 mm² |  | 127 | 177 | 106 | 26 | 185 mm² |  | 46 | 75 | 97 | 56 | [50 empty] | Total Load R: 436; Total Load Y: 427; Total Load B: 364; Total Load N: 133 | 436 | 364 | 32.397 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN1 | 23.234011, 56.522985 | 272 | Ground (GMT) |  | 1000 | 28/05/2026, 14:24 | 1 | 243 | 243 | 243 | 425 | 418 | 425 | [18 empty] | 185 mm² |  | 13 | 75 | 17 | 47 | 185 mm² |  | 124 | 31 | 55 | 22 | 185 mm² |  | 60 | 220 | 135 | 150 | [56 empty] | Total Load R: 197; Total Load Y: 326; Total Load B: 207; Total Load N: 219 | 326 | 197 | 23.9976 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 | 23.234011, 56.522985 | 272 | Ground (GMT) | 3 | 1000 | 09/06/2026, 21:07 | 2 | 249 | 250 | 247 | 435 | 430 | 430 | [18 empty] | 185 mm² |  | 1 | 8 | 17 | 8 | 185 mm² |  | 46 | 22 | 39 | 14 | 185 mm² |  | 113 | 182 | 175 | 87 | [56 empty] | Total Load R: 160; Total Load Y: 212; Total Load B: 231; Total Load N: 109 | 231 | 160 | 17.4045 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 |  | 273 | Ground (GMT) |  | 1000 | 28/05/2026, 14:16 | 1 | 243 | 246 | 243 | 425 | 419 | 423 | 185 mm² |  | 87 | 66 | 60 | 30 | 185 mm² |  | 226 | 140 | 150 | 90 | 185 mm² |  | 59 | 5 | 33 | 23 | 185 mm² |  | 30 | 67 | 24 | 20 | 185 mm² |  | 59 | 57 | 66 | 10 | [62 empty] | Total Load R: 461; Total Load Y: 335; Total Load B: 333; Total Load N: 173 | 461 | 333 | 33.9352 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 |  | 273 | Ground (GMT) | 3 | 1000 | 09/06/2026, 21:00 | 2 | 247 | 249 | 247 | 431 | 427 | 416 | 185 mm² |  | 59 | 69 | 37 | 30 | 185 mm² |  | 257 | 159 | 142 | 105 | 185 mm² |  | 50 | 24 | 7 | 13 | 185 mm² |  | 14 | 26 | 25 | 17 | 185 mm² |  | 43 | 58 | 36 | 7 | [62 empty] | Total Load R: 423; Total Load Y: 336; Total Load B: 247; Total Load N: 172 | 423 | 247 | 31.5775 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN4 | 23.232183, 56.517383 | 15 | Ground (GMT) |  | 1000 | 28/05/2026, 14:21 | 1 | 243 | 244 | 246 | 421 | 424 | 426 | 185 mm² |  | 122 | 149 | 109 | 33 | 185 mm² |  | 0 | 3 | 4 | 4 | 240 mm² |  | 62 | 62 | 42 | 51 | 120 mm² |  | 20 | 2 | 28 | 22 | 120 mm² |  | 12 | 17 | 39 | 25 | 120 mm² |  | 12 | 24 | 31 | 31 | 185 mm² |  | 1 | 1 | 1 | 1 | 120 mm² |  | 48 | 29 | 24 | 28 | [44 empty] | Total Load R: 277; Total Load Y: 287; Total Load B: 278; Total Load N: 195 | 287 | 277 | 20.9279 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN4 | 23.232183, 56.517383 | 15 | Ground (GMT) | 3 | 1000 | 09/06/2026, 21:13 | 2 | 247 | 248 | 250 | 430 | 431 | 433 | 185 mm² |  | 85 | 80 | 91 | 20 | 185 mm² |  | 0 | 4 | 2 | 3 | 240 mm² |  | 42 | 65 | 34 | 34 | 120 mm² |  | 1 | 11 | 2 | 10 | 120 mm² |  | 27 | 16 | 3 | 15 | 120 mm² |  | 27 | 40 | 74 | 36 | 185 mm² |  | 3 | 0 | 0 | 3 | 120 mm² |  | 65 | 45 | 26 | 42 | [44 empty] | Total Load R: 250; Total Load Y: 261; Total Load B: 232; Total Load N: 163 | 261 | 232 | 19.4388 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN1 |  | 274 | Ground (GMT) |  | 1000 | 28/05/2026, 14:09 | 1 | 244 | 243 | 246 | 419 | 426 | 424 | [18 empty] | 240 mm² |  | 86 | 75 | 109 | 32 | 240 mm² |  | 107 | 50 | 120 | 47 | 240 mm² |  | 71 | 85 | 65 | 53 | 240 mm² |  | 85 | 70 | 93 | 22 | 240 mm² |  | 85 | 34 | 35 | 35 | [44 empty] | Total Load R: 434; Total Load Y: 314; Total Load B: 422; Total Load N: 189 | 434 | 314 | 31.4967 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 |  | 274 | Ground (GMT) | 3 | 1000 | 09/06/2026, 20:43 | 2 | 247 | 246 | 249 | 426 | 431 | 429 | [18 empty] | 240 mm² |  | 53 | 118 | 69 | 59 | 240 mm² |  | 74 | 40 | 108 | 42 | 240 mm² |  | 42 | 59 | 71 | 14 | 240 mm² |  | 42 | 38 | 105 | 20 | 240 mm² |  | 32 | 27 | 24 | 35 | [44 empty] | Total Load R: 243; Total Load Y: 282; Total Load B: 377; Total Load N: 170 | 377 | 243 | 27.8171 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN6 | 23.230901, 56.519655 | 283 | Ground (GMT) | 3 | 1000 | 09/06/2026, 21:53 | 1 | 240 | 240 | 243 | 414 | 420 | 418 | [6 empty] | 185 mm² |  | 62 | 109 | 101 | 30 | 185 mm² |  | 101 | 45 | 83 | 48 | 185 mm² |  | 27 | 8 | 3 | 16 | 185 mm² |  | 88 | 100 | 47 | 32 | 185 mm² |  | 249 | 108 | 135 | 48 | 185 mm² |  | 83 | 104 | 130 | 27 | 185 mm² |  | 142 | 156 | 141 | 22 | [44 empty] | Total Load R: 752; Total Load Y: 630; Total Load B: 640; Total Load N: 223 | 752 | 630 | 53.9236 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN6 | 23.230901, 56.519655 | 283 | Ground (GMT) | 3 | 1000 | 09/06/2026, 22:00 | 2 | 246 | 246 | 247 | 426 | 428 | 426 | [6 empty] | 185 mm² |  | 67 | 64 | 34 | 32 | 185 mm² |  | 37 | 38 | 15 | 23 | 185 mm² |  | 37 | 11 | 15 | 20 | 185 mm² |  | 61 | 51 | 72 | 14 | 185 mm² |  | 116 | 123 | 202 | 69 | 185 mm² |  | 99 | 114 | 127 | 24 | 185 mm² |  | 35 | 89 | 52 | 32 | [44 empty] | Total Load R: 452; Total Load Y: 490; Total Load B: 517; Total Load N: 214 | 517 | 452 | 38.147 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN6 | 23.23584, 56.519982 | 922 | Ground (GMT) |  | 1000 | 28/05/2026, 13:59 | 1 | 244 | 244 | 247 | 423 | 428 | 427 | [6 empty] | 120 mm² |  | 94 | 67 | 45 | 24 | 120 mm² |  | 37 | 6 | 28 | 23 | 185 mm² |  | 0 | 0 | 0 | 0 | 240 mm² |  | 19 | 82 | 69 | 21 | 240 mm² |  | 32 | 51 | 32 | 15 | [56 empty] | Total Load R: 182; Total Load Y: 206; Total Load B: 174; Total Load N: 83 | 206 | 174 | 15.0927 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN6 | 23.23584, 56.519982 | 922 | Ground (GMT) | 3 | 1000 | 09/06/2026, 20:44 | 2 | 248 | 247 | 249 | 430 | 433 | 430 | [6 empty] | 120 mm² |  | 75 | 69 | 84 | 30 | 120 mm² |  | 20 | 14 | 29 | 8 | 185 mm² |  | 0 | 0 | 0 | 0 | 240 mm² |  | 30 | 84 | 59 | 10 | 240 mm² |  | 44 | 47 | 90 | 41 | [56 empty] | Total Load R: 169; Total Load Y: 214; Total Load B: 262; Total Load N: 89 | 262 | 169 | 19.5133 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 |  | 275 | Ground (GMT) |  | 1000 | 28/05/2026, 14:00 | 1 | 245 | 244 | 248 | 422 | 430 | 424 | 185 mm² |  | 87 | 54 | 49 | 35 | 185 mm² |  | 12 | 14 | 14 | 3 | 185 mm² |  | 46 | 39 | 4 | 34 | 185 mm² |  | 154 | 97 | 118 | 60 | 185 mm² |  | 57 | 74 | 34 | 28 | 185 mm² |  | 20 | 9 | 10 | 9 | [56 empty] | Total Load R: 376; Total Load Y: 287; Total Load B: 229; Total Load N: 169 | 376 | 229 | 27.4828 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 |  | 275 | Ground (GMT) |  | 1000 | 09/06/2026, 20:52 | 2 | 251 | 248 | 249 | 431 | 434 | 431 | 185 mm² |  | 25 | 14 | 25 | 8 | 185 mm² |  | 0 | 19 | 15 | 25 | 185 mm² |  | 25 | 35 | 6 | 33 | 185 mm² |  | 136 | 76 | 83 | 61 | 185 mm² |  | 39 | 58 | 24 | 46 | 185 mm² |  | 23 | 1 | 4 | 19 | [56 empty] | Total Load R: 248; Total Load Y: 203; Total Load B: 157; Total Load N: 192 | 248 | 157 | 18.5135 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN6 | 23.234252, 56.523602 | 281 | Ground (GMT) |  | 1000 | 28/05/2026, 13:50 | 1 | 238 | 238 | 241 | 412 | 416 | 414 | [6 empty] | 120 mm² |  | 75 | 67 | 39 | 29 | 120 mm² |  | 12 | 40 | 47 | 30 | 185 mm² |  | 87 | 91 | 154 | 48 | 185 mm² |  | 47 | 16 | 0 | 29 | 185 mm² |  | 106 | 70 | 115 | 33 | [56 empty] | Total Load R: 327; Total Load Y: 284; Total Load B: 355; Total Load N: 169 | 355 | 284 | 25.333 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN6 | 23.234252, 56.523602 | 281 | Ground (GMT) | 3 | 1000 | 09/06/2026, 20:37 | 2 | 242 | 241 | 243 | 418 | 412 | 420 | [6 empty] | 120 mm² |  | 76 | 48 | 56 | 15 | 120 mm² |  | 27 | 43 | 33 | 12 | 185 mm² |  | 70 | 60 | 62 | 19 | 185 mm² |  | 50 | 34 | 25 | 27 | 185 mm² |  | 87 | 65 | 63 | 26 | [56 empty] | Total Load R: 310; Total Load Y: 250; Total Load B: 239; Total Load N: 99 | 310 | 239 | 22.4439 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 |  | 276 | Ground (GMT) |  | 500 | 28/05/2026, 13:46 | 1 | 241 | 242 | 245 | 418 | 421 | 421 | 185 mm² |  | 65 | 30 | 123 | 39 | 120 mm² |  | 99 | 133 | 62 | 65 | 185 mm² |  | 100 | 51 | 131 | 17 | 185 mm² |  | 45 | 60 | 58 | 14 | 185 mm² |  | 99 | 66 | 94 | 21 | [62 empty] | Total Load R: 408; Total Load Y: 340; Total Load B: 468; Total Load N: 156 | 468 | 340 | 67.7661 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN1 |  | 276 | Ground (GMT) | 3 | 500 | 09/06/2026, 20:35 | 2 | 245 | 245 | 248 | 423 | 428 | 424 | 185 mm² |  | 73 | 32 | 90 | 16 | 185 mm² |  | 50 | 112 | 24 | 72 | 185 mm² |  | 120 | 101 | 88 | 50 | 185 mm² |  | 13 | 30 | 16 | 16 | 185 mm² |  | 93 | 40 | 52 | 70 | [62 empty] | Total Load R: 349; Total Load Y: 315; Total Load B: 270; Total Load N: 224 | 349 | 270 | 51.1395 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN6 | 23.231087, 56.522025 | 280 | Ground (GMT) |  | 500 | 28/05/2026, 13:39 | 1 | 242 | 243 | 246 | 420 | 425 | 424 | [12 empty] | 185 mm² |  | 182 | 66 | 114 | 20 | 185 mm² |  | 32 | 60 | 87 | 22 | 185 mm² |  | 86 | 87 | 85 | 11 | [62 empty] | Total Load R: 300; Total Load Y: 213; Total Load B: 286; Total Load N: 53 | 300 | 213 | 43.6477 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN6 | 23.231087, 56.522025 | 280 | Ground (GMT) | 3 | 500 | 09/06/2026, 20:29 | 2 | 246 | 246 | 248 | 425 | 430 | 428 | [12 empty] | 185 mm² |  | 60 | 66 | 82 | 25 | 185 mm² |  | 27 | 73 | 85 | 30 | 185 mm² |  | 98 | 76 | 84 | 20 | [62 empty] | Total Load R: 185; Total Load Y: 215; Total Load B: 251; Total Load N: 75 | 251 | 185 | 36.9533 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN8 |  | 129 | Ground (GMT) |  | 500 | 04/05/2026, 09:25 | 1 | 245 | 245 | 248 | 424 | 428 | 427 | [12 empty] | 240 mm² |  | 197 | 160 | 176 | 40 | [6 empty] | 240 mm² |  | 130 | 147 | 136 | 65 | [62 empty] | Total Load R: 327; Total Load Y: 307; Total Load B: 312; Total Load N: 105 | 327 | 307 | 48.0291 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN2 |  | 279 | Ground (GMT) |  | 500 | 03/05/2026, 09:24 | 1 | 245 | 245 | 247 | 424 | 428 | 428 | [6 empty] | 240 mm² |  | 151 | 133 | 143 | 40 | 240 mm² |  | 90 | 80 | 91 | 35 | [74 empty] | Total Load R: 241; Total Load Y: 213; Total Load B: 234; Total Load N: 75 | 241 | 213 | 35.3976 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN2 | 23.230764, 56.523867 | 278 | Ground (GMT) |  | 1000 | 03/05/2026, 09:20 | 1 | 245 | 243 | 245 | 420 | 423 | 425 | [24 empty] | 120 mm² |  | 36 | 31 | 45 | 31 | 120 mm² |  | 70 | 22 | 6 | 61 | 120 mm² |  | 50 | 39 | 37 | 12 | 120 mm² |  | 96 | 99 | 116 | 28 | [44 empty] | Total Load R: 252; Total Load Y: 191; Total Load B: 204; Total Load N: 132 | 252 | 191 | 18.332 | OK - No Upgrade | Need to Balance
Ibri | AL-MURTAFA | K_LN2 | 23.230764, 56.523867 | 278 | Ground (GMT) | 3 | 1000 | 28/05/2026, 13:29 | 2 | 245 | 245 | 248 | 425 | 430 | 428 | [24 empty] | 120 mm² |  | 81 | 77 | 107 | 21 | 120 mm² |  | 70 | 48 | 38 | 32 | 120 mm² |  | 136 | 122 | 127 | 22 | 120 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 287; Total Load Y: 247; Total Load B: 272; Total Load N: 75 | 287 | 247 | 21.1267 | OK - No Upgrade | OK - Balanced
Ibri | AL-MURTAFA | K_LN2 | 23.230764, 56.523867 | 278 | Ground (GMT) | 3 | 1000 | 09/06/2026, 20:23 | 3 | 248 | 248 | 250 | 431 | 435 | 431 | [24 empty] | 120 mm² |  | 51 | 60 | 62 | 12 | 120 mm² |  | 52 | 25 | 61 | 28 | 120 mm² |  | 77 | 102 | 104 | 42 | 120 mm² |  | 1 | 3 | 0 | 5 | [44 empty] | Total Load R: 181; Total Load Y: 190; Total Load B: 227; Total Load N: 87 | 227 | 181 | 16.9459 | OK - No Upgrade | Need to Balance

## MAZERA BIN KHATER
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Ibri | MAZERA BIN KHATER | K_LN5 | 23.211917, 56.489541 | 453 | Ground (GMT) | 3 | 1000 | 04/06/2026, 15:22 | 1 | 249 | 250 | 248 | 436 | 430 | 432 | 185 mm² |  | 18 | 36 | 14 | 17 | 185 mm² |  | 21 | 41 | 69 | 12 | 185 mm² |  | 14 | 8 | 11 | 4 | [12 empty] | 70 mm² |  | 0 | 15 | 2 | 13 | [8 empty] | Total Load R: 53; Total Load Y: 100; Total Load B: 96; Total Load N: 46 | 100 | 53 | 7.5517 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN9 | 23.190284, 56.480694 | 168 | Ground (GMT) | 3 | 1000 | 04/06/2026, 15:22 | 1 | 246 | 245 | 247 | 424 | 438 | 428 | [18 empty] | 185 mm² |  | 30 | 30 | 28 | 9 | 185 mm² |  | 45 | 7 | 53 | 35 | 120 mm² |  | 51 | 54 | 63 | 11 | 120 mm² |  | 34 | 50 | 44 | 29 | 120 mm² |  | 62 | 66 | 92 | 23 | 222 | 207 | 280 | 107 | 280 | 207 | 20.5629 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN9 | 23.19115, 56.475179 | 4141 | Ground (GMT) | 3 | 1000 | 04/06/2026, 15:14 | 1 | 245 | 246 | 247 | 426 | 426 | 430 | [30 empty] | 240 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 60 | 66 | 54 | 12 | 185 mm² |  | 41 | 81 | 77 | 38 | 101 | 147 | 131 | 50 | 147 | 101 | 10.8464 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN5 | 23.210753, 56.488183 | 1770 | Ground (GMT) | 3 | 1000 | 04/06/2026, 15:14 | 1 | 248 | 249 | 247 | 432 | 427 | 430 | [12 empty] | 185 mm² |  | 88 | 39 | 14 | 57 | 185 mm² |  | 37 | 20 | 22 | 19 | 185 mm² |  | 142 | 168 | 190 | 46 |  |  | 96 | 45 | 54 | 18 | [8 empty] | Total Load R: 363; Total Load Y: 272; Total Load B: 280; Total Load N: 140 | 363 | 272 | 27.1613 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN2 | 23.212202, 56.486057 | 1459 | Ground (GMT) | 3 | 1000 | 04/06/2026, 15:00 | 1 | 248 | 247 | 250 | 431 | 435 | 433 | 240 mm² |  | 0 | 0 | 0 | 0 | 240 mm² |  | 0 | 0 | 0 | 0 | 240 mm² |  | 62 | 48 | 90 | 20 | [26 empty] | Total Load R: 62; Total Load Y: 48; Total Load B: 90; Total Load N: 20 | 90 | 48 | 6.7186 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN2 | 23.209031, 56.485126 | 456 | Ground (GMT) | 3 | 1000 | 04/06/2026, 14:53 | 1 | 240 | 246 | 249 | 426 | 431 | 429 | 240 mm² |  | 54 | 106 | 60 | 40 | 185 mm² |  | 84 | 62 | 89 | 47 | 240 mm² |  | 60 | 71 | 55 | 20 | 185 mm² |  | 109 | 50 | 20 | 41 | 240 mm² |  | 69 | 58 | 79 | 19 | [14 empty] | Total Load R: 376; Total Load Y: 347; Total Load B: 303; Total Load N: 167 | 376 | 303 | 27.7433 | OK - No Upgrade | OK - Balanced
Ibri | MAZERA BIN KHATER | K_LN9 | 23.190353, 56.477443 | 1511 | Ground (GMT) | 3 | 1000 | 04/06/2026, 14:47 | 1 | 247 | 247 | 249 | 425 | 431 | 429 | 185 mm² |  | 118 | 33 | 31 | 88 | 185 mm² |  | 45 | 28 | 60 | 22 | [32 empty] | Total Load R: 163; Total Load Y: 61; Total Load B: 91; Total Load N: 110 | 163 | 61 | 11.9988 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN9 | 23.193563, 56.477946 | 167 | Ground (GMT) | 3 | 1000 | 04/06/2026, 14:41 | 1 | 247 | 246 | 249 | 425 | 431 | 430 | 185 mm² |  | 141 | 143 | 139 | 28 | 185 mm² |  | 63 | 61 | 53 | 15 | 185 mm² |  | 29 | 47 | 19 | 20 | [26 empty] | Total Load R: 233; Total Load Y: 251; Total Load B: 211; Total Load N: 63 | 251 | 211 | 18.4767 | OK - No Upgrade | OK - Balanced
Ibri | MAZERA BIN KHATER | K_LN2 | 23.215795, 56.487197 | 138 | Ground (GMT) | 3 | 1000 | 04/06/2026, 14:33 | 1 | 247 | 246 | 249 | 427 | 432 | 432 | 185 mm² |  | 144 | 152 | 180 | 47 | 240 mm² |  | 104 | 95 | 58 | 51 | 240 mm² |  | 70 | 101 | 114 | 25 | 185 mm² |  | 140 | 101 | 62 | 45 | 240 mm² |  | 115 | 150 | 165 | 25 | [14 empty] | Total Load R: 573; Total Load Y: 599; Total Load B: 579; Total Load N: 193 | 599 | 573 | 44.3012 | OK - No Upgrade | OK - Balanced
Ibri | MAZERA BIN KHATER | K_LN9 | 23.210161, 56.489987 | 522 | Ground (GMT) | 3 | 1000 | 04/06/2026, 14:27 | 1 | 249 | 248 | 251 | 429 | 434 | 432 | [12 empty] | 240 mm² |  | 33 | 83 | 104 | 65 | 185 mm² |  | 121 | 94 | 79 | 37 | 240 mm² |  | 45 | 51 | 49 | 15 | 185 mm² |  | 65 | 20 | 0 | 42 | [8 empty] | Total Load R: 264; Total Load Y: 248; Total Load B: 232; Total Load N: 159 | 264 | 232 | 19.6165 | OK - No Upgrade | OK - Balanced
Ibri | MAZERA BIN KHATER | K_LN2 | 23.213027, 56.486715 | 140 | Ground (GMT) | 3 | 1000 | 04/06/2026, 14:26 | 1 | 2249 | 248 | 250 | 430 | 435 | 433 | [6 empty] | 120 mm² |  | 112 | 96 | 178 | 62 | 120 mm² |  | 185 | 91 | 152 | 91 | [26 empty] | Total Load R: 297; Total Load Y: 187; Total Load B: 330; Total Load N: 153 | 330 | 187 | 24.5778 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN2 | 23.215066, 56.489653 | 137 | Ground (GMT) | 3 | 1000 | 04/06/2026, 14:19 | 1 | 247 | 245 | 246 | 425 | 232 | 429 | [12 empty] | 185 mm² |  | 0 | 0 | 12 | 12 | 185 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 60 | 73 | 59 | 22 | 185 mm² |  | 100 | 169 | 87 | 68 |  |  | Total Load R: 160; Total Load Y: 242; Total Load B: 158; Total Load N: 102 | 242 | 158 | 17.8141 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN2 | 23.215173, 56.49101 | 136 | Ground (GMT) | 3 | 1000 | 04/06/2026, 14:12 | 1 | 248 | 247 | 250 | 428 | 433 | 431 | [30 empty] | 240 mm² |  | 64 | 82 | 40 | 10 | 240 mm² |  | 92 | 75 | 64 | 19 | 240 mm² |  | 46 | 49 | 100 | 42 | 202 | 206 | 204 | 71 | 206 | 202 | 15.2711 | OK - No Upgrade | OK - Balanced
Ibri | MAZERA BIN KHATER | K_LN5 | 23.214676, 56.4911 | 135 | Ground (GMT) |  | 1000 | 04/06/2026, 14:07 | 1 | 250 | 247 | 248 | 430 | 433 | 430 | 185 mm² | [17 empty] | 120 mm² |  | 62 | 14 | 15 | 46 | 185 mm² |  | 1 | 9 | 9 | 2 | 185 mm² |  | 1 | 3 | 60 | 57 | 185 mm² |  | 50 | 67 | 58 | 14 | 185 mm² |  | 125 | 231 | 75 | 128 | 239 | 324 | 217 | 247 | 324 | 217 | 24.1309 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN45 | 23.218842, 56.493274 | 107 | Ground (GMT) | 3 | 1000 |  | 1 | 248 | 248 | 252 | 429 | 436 | 435 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | MAZERA BIN KHATER | K_LN3 | 23.197241, 56.463819 | 156 | Pole (PMT) |  | 315 | 03/06/2026, 15:44 | 1 | 245 | 244 | 245 | 419 | 425 | 425 | 185 mm² |  | 90 | 14 | 142 | 106 | 185 mm² |  | 155 | 158 | 154 | 25 | [32 empty] | Total Load R: 245; Total Load Y: 172; Total Load B: 296; Total Load N: 131 | 296 | 172 | 68.1955 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN3 | 23.194244, 56.466769 | 4444 | Pole (PMT) |  | 100 | 03/06/2026, 15:30 | 1 | 247 | 245 | 248 | 427 | 431 | 427 | 185 mm² |  | 16 | 36 | 13 | 20 | [38 empty] | Total Load R: 16; Total Load Y: 36; Total Load B: 13; Total Load N: 20 | 36 | 13 | 26.6251 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN3 | 23.196802, 56.466041 | 1989 | Ground (GMT) |  | 1000 | 03/06/2026, 15:23 | 1 | 247 | 246 | 249 | 426 | 433 | 428 | [12 empty] | 185 mm² |  | 66 | 43 | 49 | 15 | 185 mm² |  | 6 | 91 | 43 | 57 | [6 empty] | 185 mm² |  | 53 | 52 | 59 | 12 | 185 mm² |  | 54 | 35 | 32 | 10 | 185 mm² |  | 47 | 64 | 66 | 7 | 226 | 285 | 249 | 101 | 285 | 226 | 21.0288 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN3 | 23.196921, 56.46952 | 1599 | Ground (GMT) |  | 1000 | 03/06/2026, 15:13 | 1 | 246 | 248 | 249 | 428 | 429 | 434 | 185 mm² |  | 114 | 103 | 62 | 38 | 185 mm² |  | 19 | 25 | 19 | 7 | 185 mm² |  | 47 | 41 | 35 | 15 | 120 mm² |  | 38 | 61 | 70 | 37 | 185 mm² |  | 50 | 68 | 24 | 44 | 185 mm² |  | 12 | 0 | 15 | 12 | [8 empty] | Total Load R: 280; Total Load Y: 298; Total Load B: 225; Total Load N: 153 | 298 | 225 | 22.0913 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN3 | 23.199814, 56.47906 | 1494 | Ground (GMT) |  | 1000 | 03/06/2026, 14:59 | 1 | 248 | 247 | 249 | 429 | 433 | 431 | 185 mm² |  | 63 | 41 | 109 | 56 | 185 mm² |  | 61 | 73 | 67 | 20 | 185 mm² |  | 37 | 37 | 43 | 10 | 185 mm² |  | 55 | 29 | 62 | 34 | 185 mm² |  | 117 | 83 | 26 | 89 | 185 mm² |  | 78 | 48 | 66 | 22 | [8 empty] | Total Load R: 411; Total Load Y: 311; Total Load B: 373; Total Load N: 231 | 411 | 311 | 30.5393 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN3 | 23.201869, 56.470325 | 1794 | Ground (GMT) |  | 1000 | 03/06/2026, 14:38 | 1 | 239 | 241 | 243 | 415 | 414 | 423 | [6 empty] | 240 mm² |  | 130 | 88 | 157 | 28 | 185 mm² |  | 312 | 206 | 175 | 94 | [6 empty] | 185 mm² |  | 196 | 132 | 119 | 73 | 185 mm² |  | 100 | 109 | 68 | 42 | [8 empty] | Total Load R: 738; Total Load Y: 535; Total Load B: 519; Total Load N: 237 | 738 | 519 | 53.0475 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN3 | 23.199581, 56.473115 | 154 | Ground (GMT) |  | 1000 | 03/06/2026, 14:30 | 1 | 243 | 244 | 246 | 423 | 424 | 426 | [18 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 197 | 159 | 236 | 75 | 240 mm² |  | 123 | 116 | 145 | 29 | 240 mm² |  | 134 | 42 | 115 | 73 | 240 mm² |  | 198 | 156 | 112 | 50 | 652 | 473 | 608 | 227 | 652 | 473 | 47.7693 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN3 | 23.20355, 56.475108 | 153 | Ground (GMT) |  | 1000 | 03/06/2026, 14:19 | 1 | 244 | 244 | 247 | 425 | 425 | 428 | 185 mm² |  | 83 | 81 | 112 | 10 | 185 mm² |  | 122 | 104 | 134 | 25 | 185 mm² |  | 42 | 4 | 47 | 37 | 185 mm² |  | 13 | 27 | 39 | 18 | [6 empty] | 185 mm² |  | 121 | 94 | 91 | 20 | [8 empty] | Total Load R: 381; Total Load Y: 310; Total Load B: 423; Total Load N: 110 | 423 | 310 | 31.1379 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN3 | 23.204945, 56.47753 | 152 | Ground (GMT) |  | 1000 | 03/06/2026, 14:01 | 1 | 246 | 247 | 250 | 426 | 430 | 433 | [6 empty] | 185 mm² |  | 189 | 126 | 104 | 69 | 185 mm² |  | 81 | 83 | 95 | 16 | 185 mm² |  | 66 | 73 | 89 | 25 | 185 mm² |  | 24 | 32 | 15 | 17 | 185 mm² |  | 129 | 197 | 163 | 32 | [8 empty] | Total Load R: 489; Total Load Y: 511; Total Load B: 466; Total Load N: 159 | 511 | 466 | 37.7043 | OK - No Upgrade | OK - Balanced
Ibri | MAZERA BIN KHATER | K_LN9 | 23.197321, 56.475363 | 1535 | Pole (PMT) |  | 315 | 02/06/2026, 15:45 | 1 | 244 | 243 | 246 | 420 | 426 | 421 | 120 mm² |  | 135 | 149 | 116 | 29 | 240 mm² |  | 118 | 140 | 96 | 36 | [32 empty] | Total Load R: 253; Total Load Y: 289; Total Load B: 212; Total Load N: 65 | 289 | 212 | 66.7417 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN9 | 23.196255, 56.480698 | 166 | Ground (GMT) |  | 1000 | 02/06/2026, 15:40 | 1 | 245 | 245 | 248 | 427 | 430 | 426 | 240 mm² |  | 22 | 28 | 27 | 10 | 240 mm² |  | 92 | 137 | 58 | 57 | 240 mm² |  | 185 | 125 | 110 | 53 | 240 mm² |  | 123 | 113 | 117 | 19 | 240 mm² |  | 180 | 148 | 136 | 42 | 185 mm² |  | 28 | 79 | 32 | 38 | 185 mm² |  | 20 | 34 | 37 | 10 |  |  | Total Load R: 650; Total Load Y: 664; Total Load B: 517; Total Load N: 229 | 664 | 517 | 49.1085 | OK - No Upgrade | OK - Balanced
Ibri | MAZERA BIN KHATER | K_LN9 | 23.202283, 56.483477 | 1782 | Ground (GMT) |  | 1000 | 02/06/2026, 15:30 | 1 | 248 | 247 | 250 | 428 | 433 | 430 | 185 mm² |  | 31 | 28 | 9 | 17 | 185 mm² |  | 40 | 76 | 88 | 22 | 185 mm² |  | 6 | 31 | 0 | 17 | 185 mm² |  | 71 | 110 | 58 | 11 | 185 mm² |  | 18 | 11 | 5 | 27 | 240 mm² |  | 32 | 7 | 26 | 12 | 240 mm² |  | 11 | 12 | 0 | 4 | 240 mm² |  | 16 | 19 | 28 | 13 | 225 | 294 | 214 | 123 | 294 | 214 | 21.7947 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN9 | 23.201836, 56.484575 | 1775 | Ground (GMT) |  | 1000 | 02/06/2026, 15:22 | 1 | 248 | 247 | 250 | 427 | 431 | 431 | 185 mm² |  | 191 | 115 | 117 | 74 | 185 mm² |  | 27 | 11 | 13 | 14 | 185 mm² |  | 45 | 17 | 20 | 20 | 185 mm² |  | 45 | 67 | 66 | 17 | 185 mm² |  | 38 | 35 | 32 | 9 | 185 mm² |  | 46 | 27 | 46 | 24 | [8 empty] | Total Load R: 392; Total Load Y: 272; Total Load B: 294; Total Load N: 158 | 392 | 272 | 28.9918 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN9 | 23.204953, 56.489054 | 1333 | Pole (PMT) |  | 315 | 02/06/2026, 15:08 | 1 | 247 | 247 | 249 | 426 | 431 | 431 | 185 mm² |  | 35 | 47 | 76 | 34 | 120 mm² |  | 153 | 42 | 111 | 108 | [32 empty] | Total Load R: 188; Total Load Y: 89; Total Load B: 187; Total Load N: 142 | 188 | 89 | 44.037 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN9 | 23.205861, 56.486558 | 518 | Ground (GMT) |  | 1000 | 02/06/2026, 15:04 | 1 | 249 | 247 | 250 | 432 | 429 | 432 | 240 mm² |  | 11 | 109 | 29 | 74 | 240 mm² |  | 62 | 21 | 24 | 39 | 240 mm² |  | 34 | 111 | 126 | 90 | 240 mm² |  | 2 | 17 | 21 | 16 | 185 mm² |  | 60 | 76 | 88 | 29 | [14 empty] | Total Load R: 169; Total Load Y: 334; Total Load B: 288; Total Load N: 248 | 334 | 169 | 24.9914 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN4 | 23.218348, 56.494045 | 1651 | Ground (GMT) |  | 500 | 02/06/2026, 14:59 | 1 | 250 | 247 | 247 | 433 | 434 | 427 | 240 mm² |  | 89 | 75 | 59 | 95 | 120 mm² |  | 1 | 12 | 9 | 14 | 185 mm² |  | 30 | 72 | 90 | 15 | 120 mm² |  | 102 | 71 | 137 | 84 | 185 mm² |  | 0 | 80 | 2 | 20 | 185 mm² |  | 35 | 5 | 65 | 48 | [8 empty] | Total Load R: 257; Total Load Y: 315; Total Load B: 362; Total Load N: 276 | 362 | 257 | 54.2984 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN9 | 23.207756, 56.488665 | 1908 | Ground (GMT) |  | 1000 | 02/06/2026, 14:54 | 1 | 247 | 247 | 249 | 427 | 435 | 434 | [6 empty] | 185 mm² |  | 16 | 6 | 22 | 8 | 240 mm² |  | 48 | 15 | 21 | 30 | 240 mm² |  | 12 | 1 | 31 | 20 | 240 mm² |  | 45 | 23 | 48 | 24 | 240 mm² |  | 9 | 46 | 35 | 34 | 185 mm² |  | 26 | 19 | 5 | 18 |  |  | Total Load R: 156; Total Load Y: 110; Total Load B: 162; Total Load N: 134 | 162 | 110 | 11.9813 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN4 | 23.218217, 56.492079 | 109 | Ground (GMT) |  | 1000 | 02/06/2026, 14:49 | 1 | 248 | 246 | 247 | 429 | 430 | 427 | 185 mm² |  | 23 | 35 | 1 | 20 | [6 empty] | 120 mm² |  | 0 | 6 | 0 | 6 | 120 mm² |  | 44 | 10 | 13 | 31 | 185 mm² |  | 124 | 57 | 72 | 84 | 185 mm² |  | 18 | 14 | 28 | 13 | 185 mm² |  | 115 | 135 | 100 | 34 | 185 mm² |  | 69 | 112 | 89 | 39 | 393 | 369 | 303 | 227 | 393 | 303 | 29.2019 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN9 | 23.207532, 56.489453 | 700 | Ground (GMT) |  | 1000 | 02/06/2026, 14:47 | 1 | 245 | 245 | 247 | 421 | 429 | 427 | 185 mm² |  | 125 | 116 | 90 | 35 | 185 mm² |  | 79 | 41 | 36 | 18 | 185 mm² |  | 77 | 46 | 52 | 19 | 185 mm² |  | 58 | 76 | 83 | 32 | 185 mm² |  | 113 | 79 | 72 | 34 | 240 mm² |  | 189 | 211 | 201 | 29 | [6 empty] | 120 mm² |  | 13 | 17 | 0 | 14 | 654 | 586 | 534 | 181 | 654 | 534 | 47.6892 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN8 | 23.2178, 56.490323 | 2118 | Ground (GMT) |  | 1000 | 02/06/2026, 14:41 | 1 | 247 | 245 | 245 | 427 | 429 | 426 | 240 mm² |  | 114 | 105 | 102 | 2 | 240 mm² |  | 111 | 117 | 125 | 2 | 240 mm² |  | 40 | 110 | 108 | 61 | 240 mm² |  | 99 | 90 | 91 | 128 | 185 mm² |  | 190 | 252 | 240 | 66 | [14 empty] | Total Load R: 554; Total Load Y: 674; Total Load B: 666; Total Load N: 259 | 674 | 554 | 49.8481 | OK - No Upgrade | OK - Balanced
Ibri | MAZERA BIN KHATER | K_LN8 | 23.21666, 56.487319 | 54 | Ground (GMT) |  | 500 | 02/06/2026, 14:33 | 1 | 237 | 237 | 239 | 411 | 415 | 414 | 185 mm² |  | 10 | 0 | 6 | 6 | 185 mm² |  | 10 | 0 | 8 | 6 | [32 empty] | Total Load R: 20; Total Load Y: 0; Total Load B: 14; Total Load N: 12 | 20 | 0 | 2.8475 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN8 | 23.216693, 56.487033 | 55 | Ground (GMT) |  | 1000 | 02/06/2026, 14:29 | 1 | 247 | 247 | 249 | 426 | 433 | 431 | 300 mm² |  | 180 | 144 | 95 | 128 | [38 empty] | Total Load R: 180; Total Load Y: 144; Total Load B: 95; Total Load N: 128 | 180 | 95 | 13.2814 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN8 | 23.217389, 56.48807 | 801 | Ground (GMT) |  | 1000 | 02/06/2026, 14:24 | 1 | 247 | 248 | 250 | 430 | 434 | 434 | 240 mm² |  | 38 | 28 | 38 | 5 | 185 mm² |  | 93 | 94 | 42 | 16 | 185 mm² |  | 67 | 36 | 38 | 13 | 185 mm² |  | 129 | 56 | 78 | 72 | 185 mm² |  | 105 | 63 | 89 | 48 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 95 | 68 | 76 | 23 |  |  | Total Load R: 527; Total Load Y: 345; Total Load B: 361; Total Load N: 177 | 527 | 345 | 39.25 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.144501, 56.476112 | 203 | Pole (PMT) |  | 100 | 02/06/2026, 13:59 | 1 | 245 | 246 | 248 | 425 | 429 | 428 | 120 mm² |  | 14 | 1 | 5 | 10 | [38 empty] | Total Load R: 14; Total Load Y: 1; Total Load B: 5; Total Load N: 10 | 14 | 1 | 10.3057 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.140185, 56.468801 | 004513 | Pole (PMT) |  | 100 | 02/06/2026, 13:54 | 1 | 259 | 258 | 257 | 451 | 442 | 432 | 185 mm² |  | 22 | 9 | 12 | 10 | [38 empty] | Total Load R: 22; Total Load Y: 9; Total Load B: 12; Total Load N: 10 | 22 | 9 | 17.1854 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.140185, 56.468801 | 04513 | Pole (PMT) |  | 100 |  | 1 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | MAZERA BIN KHATER | K_LN6 | 23.141048, 56.468732 | 1309 | Ground (GMT) |  | 1000 | 02/06/2026, 13:46 | 1 | 244 | 245 | 245 | 415 | 422 | 422 | 120 mm² |  | 25 | 0 | 130 | 24 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 0 | 0 | 0 | 0 | 70 mm² |  | 40 | 33 | 36 | 8 | [20 empty] | Total Load R: 65; Total Load Y: 33; Total Load B: 166; Total Load N: 32 | 166 | 33 | 11.9321 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.141077, 56.468749 | 1308 | Ground (GMT) |  | 1000 | 02/06/2026, 13:42 | 1 | 231 | 244 | 215 | 422 | 416 | 427 | 240 mm² |  | 43 | 25 | 46 | 25 | 240 mm² |  | 55 | 62 | 36 | 49 | 120 mm² |  | 0 | 0 | 0 | 0 | [26 empty] | Total Load R: 98; Total Load Y: 87; Total Load B: 82; Total Load N: 74 | 98 | 82 | 7.1631 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.143419, 56.470776 | 185 | Ground (GMT) |  | 1000 | 01/06/2026, 16:07 | 1 | 245 | 245 | 246 | 425 | 419 | 428 | 120 mm² |  | 117 | 61 | 69 | 39 | 120 mm² |  | 54 | 17 | 73 | 40 | 120 mm² |  | 82 | 54 | 109 | 57 | 120 mm² |  | 69 | 111 | 58 | 44 | [20 empty] | Total Load R: 322; Total Load Y: 243; Total Load B: 309; Total Load N: 180 | 322 | 243 | 23.7031 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.141499, 56.467984 | 188 | Ground (GMT) |  | 1000 | 01/06/2026, 15:57 | 1 | 233 | 233 | 235 | 404 | 407 | 404 | 185 mm² |  | 34 | 30 | 6 | 6 | 185 mm² |  | 4 | 11 | 8 | 7 | 185 mm² |  | 31 | 40 | 24 | 9 | 185 mm² |  | 13 | 131 | 87 | 96 | 185 mm² |  | 66 | 25 | 51 | 45 | [14 empty] | Total Load R: 148; Total Load Y: 237; Total Load B: 176; Total Load N: 163 | 237 | 148 | 16.584 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.141512, 56.467996 | 1883 | Pole (PMT) |  | 315 | 01/06/2026, 15:49 | 1 | 242 | 244 | 245 | 421 | 426 | 424 | 185 mm² |  | 40 | 11 | 30 | 23 | 185 mm² |  | 52 | 45 | 34 | 18 | [32 empty] | Total Load R: 92; Total Load Y: 56; Total Load B: 64; Total Load N: 41 | 92 | 56 | 21.2971 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.117024, 56.457922 | 208 | Pole (PMT) |  | 100 | 01/06/2026, 15:33 | 1 | 245 | 245 | 256 | 424 | 427 | 428 | 120 mm² |  | 4 | 0 | 12 | 7 | [38 empty] | Total Load R: 4; Total Load Y: 0; Total Load B: 12; Total Load N: 7 | 12 | 0 | 8.8127 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.102693, 56.456604 | 210 | Pole (PMT) |  | 100 | 01/06/2026, 15:23 | 1 | 245 | 243 | 244 | 423 | 424 | 424 | 185 mm² |  | 18 | 28 | 35 | 20 | [38 empty] | Total Load R: 18; Total Load Y: 28; Total Load B: 35; Total Load N: 20 | 35 | 18 | 25.643 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.10849, 56.457226 | 209 | Pole (PMT) |  | 100 | 01/06/2026, 15:17 | 1 | 244 | 240 | 244 | 422 | 424 | 420 | 120 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 58 | 23 | 48 | [32 empty] | Total Load R: 0; Total Load Y: 58; Total Load B: 23; Total Load N: 48 | 58 | 0 | 42.3937 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.108702, 56.463567 | 211 | Pole (PMT) |  | 100 | 01/06/2026, 15:13 | 1 | 249 | 248 | 246 | 433 | 433 | 437 | 120 mm² |  | 21 | 1 | 33 | 32 | [38 empty] | Total Load R: 21; Total Load Y: 1; Total Load B: 33; Total Load N: 32 | 33 | 1 | 24.7493 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.118898, 56.466379 | 207 | Pole (PMT) |  | 100 | 01/06/2026, 15:08 | 1 | 241 | 242 | 244 | 418 | 423 | 423 | 185 mm² |  | 45 | 27 | 32 | 15 | [38 empty] | Total Load R: 45; Total Load Y: 27; Total Load B: 32; Total Load N: 15 | 45 | 27 | 32.5799 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.136184, 56.476694 | 206 | Pole (PMT) |  | 100 | 01/06/2026, 15:03 | 1 | 244 | 244 | 245 | 423 | 425 | 425 | 120 mm² |  | 11 | 8 | 25 | 15 | [38 empty] | Total Load R: 11; Total Load Y: 8; Total Load B: 25; Total Load N: 15 | 25 | 8 | 18.3164 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.133608, 56.471421 | 205 | Pole (PMT) |  | 100 | 01/06/2026, 14:56 | 1 | 244 | 243 | 246 | 421 | 426 | 425 | 120 mm² |  | 9 | 11 | 0 | 9 | [38 empty] | Total Load R: 9; Total Load Y: 11; Total Load B: 0; Total Load N: 9 | 11 | 0 | 8.0211 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.141043, 56.474795 | 204 | Ground (GMT) |  | 1000 | 01/06/2026, 14:47 | 1 | 244 | 244 | 245 | 422 | 426 | 425 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 32 | 1 | 46 | 44 | 185 mm² |  | 97 | 51 | 86 | 40 | 185 mm² |  | 17 | 5 | 19 | 18 | [20 empty] | Total Load R: 146; Total Load Y: 57; Total Load B: 151; Total Load N: 102 | 151 | 57 | 11.037 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.141535, 56.473978 | 202 | Pole (PMT) |  | 315 | 01/06/2026, 14:39 | 1 | 243 | 244 | 246 | 422 | 426 | 426 | 120 mm² |  | 43 | 22 | 54 | 50 | 50 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 43; Total Load Y: 22; Total Load B: 54; Total Load N: 50 | 54 | 22 | 12.5302 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.139375, 56.468862 | 201 | Pole (PMT) |  | 315 | 01/06/2026, 14:34 | 1 | 243 | 244 | 245 | 422 | 425 | 425 | 185 mm² |  | 33 | 14 | 41 | 28 | 185 mm² |  | 6 | 0 | 32 | 27 | [32 empty] | Total Load R: 39; Total Load Y: 14; Total Load B: 73; Total Load N: 55 | 73 | 14 | 16.9389 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.141233, 56.472087 | 200 | Pole (PMT) |  | 315 | 01/06/2026, 14:30 | 1 | 257 | 256 | 259 | 445 | 449 | 448 | 185 mm² |  | 0 | 21 | 19 | 19 | [38 empty] | Total Load R: 0; Total Load Y: 21; Total Load B: 19; Total Load N: 19 | 21 | 0 | 5.1384 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.147203, 56.475765 | 184 | Ground (GMT) |  | 1000 | 01/06/2026, 14:25 | 1 | 244 | 244 | 247 | 421 | 426 | 426 | 185 mm² |  | 21 | 12 | 39 | 25 | 185 mm² |  | 20 | 42 | 30 | 11 | 185 mm² |  | 80 | 82 | 54 | 39 | 185 mm² |  | 13 | 1 | 0 | 13 | 185 mm² |  | 129 | 68 | 44 | 67 | [14 empty] | Total Load R: 263; Total Load Y: 205; Total Load B: 167; Total Load N: 155 | 263 | 167 | 19.1778 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.147157, 56.475743 | 1966 | Ground (GMT) |  | 1000 | 01/06/2026, 14:17 | 1 | 245 | 245 | 247 | 424 | 429 | 428 | [42 empty] | 185 mm² |  | 29 | 35 | 56 | 28 | 29 | 35 | 56 | 28 | 56 | 29 | 4.1126 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.147232, 56.477866 | 180 | Ground (GMT) |  | 500 | 01/06/2026, 14:10 | 1 | 246 | 246 | 248 | 424 | 429 | 433 | 185 mm² |  | 61 | 28 | 45 | 28 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 23 | 18 | 52 | 28 | 185 mm² |  | 60 | 0 | 11 | 59 | [20 empty] | Total Load R: 144; Total Load Y: 46; Total Load B: 108; Total Load N: 115 | 144 | 46 | 21.1504 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.149683, 56.474966 | 182 | Pole (PMT) |  | 315 | 01/06/2026, 14:03 | 1 | 243 | 243 | 245 | 420 | 424 | 424 | 185 mm² |  | 32 | 27 | 42 | 15 | 240 mm² |  | 57 | 50 | 47 | 18 | [32 empty] | Total Load R: 89; Total Load Y: 77; Total Load B: 89; Total Load N: 33 | 89 | 77 | 20.5537 | OK - No Upgrade | OK - Balanced
Ibri | MAZERA BIN KHATER | K_LN6 | 23.157497, 56.478208 | 2186 | Pole (PMT) |  | 315 | 01/06/2026, 13:58 | 1 | 245 | 24 | 247 | 426 | 429 | 427 | 185 mm² |  | 2 | 15 | 4 | 9 | [38 empty] | Total Load R: 2; Total Load Y: 15; Total Load B: 4; Total Load N: 9 | 15 | 2 | 3.5136 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.157057, 56.478452 | 4547 | Pole (PMT) |  | 100 | 01/06/2026, 13:55 | 1 | 244 | 244 | 246 | 422 | 424 | 425 | 185 mm² |  | 83 | 77 | 99 | 19 | [38 empty] | Total Load R: 83; Total Load Y: 77; Total Load B: 99; Total Load N: 19 | 99 | 77 | 72.3616 | Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.157603, 56.478336 | 179 | Pole (PMT) |  | 100 | 01/06/2026, 13:50 | 1 | 243 | 244 | 244 | 420 | 424 | 425 | 120 mm² |  | 36 | 0 | 22 | 27 | 185 mm² |  | 34 | 38 | 25 | 12 | [32 empty] | Total Load R: 70; Total Load Y: 38; Total Load B: 47; Total Load N: 39 | 70 | 38 | 50.9223 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN6 | 23.162719, 56.477119 | 4440 | Pole (PMT) |  | 315 | 01/06/2026, 13:45 | 1 | 236 | 236 | 238 | 409 | 413 | 411 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | MAZERA BIN KHATER | K_LN6 | 23.164738, 56.47458 | 178 | Pole (PMT) |  | 100 | 01/06/2026, 13:32 | 1 | 249 | 249 | 251 | 433 | 436 | 435 | 185 mm² |  | 0 | 0 | 2 | 2 | 50 mm² |  | 5 | 7 | 5 | 2 | [32 empty] | Total Load R: 5; Total Load Y: 7; Total Load B: 7; Total Load N: 4 | 7 | 5 | 5.2498 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN9 | 23.212251, 56.491267 | 1437 | Pole (PMT) |  | 315 | 01/06/2026, 13:26 | 1 | 250 | 249 | 250 | 431 | 434 | 434 | 120 mm² |  | 12 | 31 | 92 | 71 | 185 mm² |  | 14 | 15 | 13 | 5 | [32 empty] | Total Load R: 26; Total Load Y: 46; Total Load B: 105; Total Load N: 76 | 105 | 26 | 24.8838 | OK - No Upgrade | Need to Balance
Ibri | MAZERA BIN KHATER | K_LN9 | 23.214472, 56.491875 | 1836 | Ground (GMT) |  | 1000 | 01/06/2026, 13:19 | 1 | 250 | 249 | 253 | 423 | 438 | 437 | 185 mm² |  | 28 | 85 | 51 | 48 | 185 mm² |  | 39 | 58 | 54 | 20 | 185 mm² |  | 213 | 138 | 153 | 58 | 240 mm² |  | 14 | 0 | 0 | 11 | [20 empty] | Total Load R: 294; Total Load Y: 281; Total Load B: 258; Total Load N: 137 | 294 | 258 | 21.5401 | OK - No Upgrade | OK - Balanced
Ibri | MAZERA BIN KHATER | K_LN6 |  | 181 | Ground (GMT) |  | 500 | 03/05/2026, 11:23 | 1 | 244 | 244 | 246 | 422 | 427 | 426 | [6 empty] | 240 mm² |  | 140 | 127 | 121 | 126 | [8 empty] | 68 | 83 | 50 | 69 | [20 empty] | Total Load R: 208; Total Load Y: 210; Total Load B: 171; Total Load N: 195 | 210 | 171 | 30.6989 | OK - No Upgrade | OK - Balanced
Ibri | MAZERA BIN KHATER | K_LN6 |  | 2147 | Ground (GMT) |  | 1000 | 03/05/2026, 11:11 | 1 | 232 | 233 | 235 | 399 | 405 | 406 | [18 empty] | 240 mm² |  | 62 | 79 | 76 | 17 | [6 empty] | 240 mm² |  | 129 | 92 | 94 | 41 | 240 mm² |  | 83 | 69 | 111 | 38 | 240 mm² |  | 123 | 128 | 117 | 21 | 397 | 368 | 398 | 117 | 398 | 368 | 27.5053 | OK - No Upgrade | OK - Balanced

## AL-ARAQI
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Ibri | AL-ARAQI | K_LN3 | 23.23748, 56.519219 | 920 | Ground (GMT) | 3 | 1000 | 13/06/2026, 14:57 | 1 | 243 | 243 | 245 | 422 | 422 | 425 | 185 mm² |  | 35 | 20 | 16 | 17 | 185 mm² |  | 141 | 109 | 129 | 64 | 185 mm² |  | 11 | 42 | 13 | 29 | 185 mm² |  | 174 | 153 | 78 | 101 | 185 mm² |  | 39 | 48 | 23 | 25 | 185 mm² |  | 78 | 119 | 69 | 25 | [8 empty] | Total Load R: 478; Total Load Y: 491; Total Load B: 328; Total Load N: 261 | 491 | 328 | 35.8884 | OK - No Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN3 | 23.240197, 56.514109 | 916 | Pole (PMT) | 3 | 315 | 13/06/2026, 14:47 | 1 | 245 | 245 | 247 | 425 | 429 | 428 | 240 mm² |  | 2 | 0 | 0 | 0 | [38 empty] | Total Load R: 2; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 2 | 0 | 0.46738 | OK - No Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN3 | 23.239621, 56.514915 | 1312 | Ground (GMT) | 3 | 1000 | 13/06/2026, 14:43 | 1 | 242 | 243 | 243 | 426 | 420 | 422 | 185 mm² |  | 142 | 86 | 80 | 30 | 120 mm² |  | 71 | 99 | 70 | 25 | 185 mm² |  | 42 | 36 | 17 | 20 | 120 mm² |  | 33 | 29 | 114 | 76 | 120 mm² |  | 158 | 137 | 227 | 46 | 120 mm² |  | 88 | 153 | 185 | 68 | 120 mm² |  | 116 | 17 | 105 | 92 |  |  | Total Load R: 650; Total Load Y: 557; Total Load B: 798; Total Load N: 357 | 798 | 557 | 58.8807 | OK - No Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN3 | 23.243248, 56.516977 | 917 | Ground (GMT) | 3 | 500 | 13/06/2026, 14:37 | 1 | 244 | 244 | 243 | 425 | 423 | 420 | 120 mm² |  | 62 | 35 | 41 | 17 | 185 mm² |  | 51 | 41 | 62 | 35 | 185 mm² |  | 12 | 4 | 12 | 9 | [26 empty] | Total Load R: 125; Total Load Y: 80; Total Load B: 115; Total Load N: 61 | 125 | 80 | 18.403 | OK - No Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN3 | 23.243265, 56.514462 | 1311 | Ground (GMT) | 3 | 1000 | 13/06/2026, 14:30 | 1 | 244 | 244 | 247 | 423 | 426 | 425 | [6 empty] | 120 mm² |  | 17 | 104 | 22 | 74 | 185 mm² |  | 89 | 150 | 76 | 74 | 120 mm² |  | 84 | 87 | 130 | 36 | 185 mm² |  | 98 | 69 | 44 | 45 | [14 empty] | Total Load R: 288; Total Load Y: 410; Total Load B: 272; Total Load N: 229 | 410 | 272 | 30.039 | OK - No Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN3 | 23.242541, 56.513524 | 913 | Ground (GMT) | 3 | 500 | 13/06/2026, 14:25 | 1 | 248 | 248 | 250 | 430 | 433 | 432 | 120 mm² |  | 34 | 39 | 26 | 16 | [38 empty] | Total Load R: 34; Total Load Y: 39; Total Load B: 26; Total Load N: 16 | 39 | 26 | 5.8093 | OK - No Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN3 | 23.25009, 56.509775 | 237 | Pole (PMT) | 3 | 315 | 13/06/2026, 14:20 | 1 | 234 | 240 | 242 | 414 | 428 | 424 | 185 mm² |  | 121 | 54 | 41 | 69 | 185 mm² |  | 76 | 87 | 103 | 22 | [32 empty] | Total Load R: 197; Total Load Y: 141; Total Load B: 144; Total Load N: 91 | 197 | 141 | 44.8453 | OK - No Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN3 | 23.250562, 56.510265 | 236 | Pole (PMT) | 3 | 315 | 13/06/2026, 14:13 | 1 | 241 | 243 | 244 | 418 | 424 | 421 | 185 mm² |  | 118 | 125 | 149 | 18 | 185 mm² |  | 197 | 129 | 129 | 65 | [32 empty] | Total Load R: 315; Total Load Y: 254; Total Load B: 278; Total Load N: 83 | 315 | 254 | 72.3997 | Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN3 | 23.256297, 56.512834 | 235 | Pole (PMT) | 3 | 315 | 13/06/2026, 14:07 | 1 | 246 | 246 | 247 | 426 | 430 | 429 | 185 mm² |  | 69 | 49 | 55 | 25 | [38 empty] | Total Load R: 69; Total Load Y: 49; Total Load B: 55; Total Load N: 25 | 69 | 49 | 16.1625 | OK - No Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN5 | 23.251066, 56.528814 | 1979 | Pole (PMT) | 3 | 100 | 13/06/2026, 13:57 | 1 | 248 | 249 | 251 | 432 | 435 | 434 | 185 mm² |  | 9 | 0 | 0 | 9 | [38 empty] | Total Load R: 9; Total Load Y: 0; Total Load B: 0; Total Load N: 9 | 9 | 0 | 6.7342 | OK - No Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN5 | 23.249021, 56.529932 | 268 | Pole (PMT) | 3 | 100 | 13/06/2026, 13:53 | 1 | 248 | 247 | 240 | 430 | 432 | 430 | 120 mm² |  | 11 | 37 | 1 | 28 | 120 mm² |  | 2 | 0 | 28 | 25 | [32 empty] | Total Load R: 13; Total Load Y: 37; Total Load B: 29; Total Load N: 53 | 37 | 13 | 27.5569 | OK - No Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN5 | 23.259223, 56.524106 | 2159 | Pole (PMT) | 3 | 315 | 13/06/2026, 13:48 | 1 | 248 | 248 | 251 | 430 | 435 | 434 | 185 mm² |  | 21 | 3 | 0 | 14 | 185 mm² |  | 0 | 0 | 0 | 3 | [32 empty] | Total Load R: 21; Total Load Y: 3; Total Load B: 0; Total Load N: 17 | 21 | 0 | 4.9652 | OK - No Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN5 | 23.256127, 56.521328 | 4579 | Ground (GMT) | 3 | 1000 | 13/06/2026, 13:40 | 1 | 249 | 249 | 251 | 429 | 429 | 432 | 185 mm² |  | 70 | 104 | 62 | 62 | 185 mm² |  | 158 | 153 | 176 | 51 | 185 mm² |  | 76 | 33 | 45 | 34 | [26 empty] | Total Load R: 304; Total Load Y: 290; Total Load B: 283; Total Load N: 147 | 304 | 283 | 22.5887 | OK - No Upgrade | OK - Balanced
Ibri | AL-ARAQI | K_LN5 | 23.255793, 56.521189 | 1523 | Pole (PMT) | 3 | 315 | 13/06/2026, 13:32 | 1 | 239 | 249 | 251 | 432 | 435 | 434 | 120 mm² |  | 27 | 17 | 44 | 22 | 120 mm² |  | 10 | 1 | 9 | 8 | [32 empty] | Total Load R: 37; Total Load Y: 18; Total Load B: 53; Total Load N: 30 | 53 | 18 | 12.5895 | OK - No Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN4 | 23.259148, 56.521872 | 1577 | Ground (GMT) | 3 | 1000 |  | 1 | 244 | 243 | 246 | [47 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL-ARAQI | K_LN02 |  | 251 | Ground (GMT) | 3 | 500 | 07/06/2026, 14:34 | 1 | 239 | 238 | 241 | 413 | 415 | 418 | [12 empty] | 185 mm² |  | 120 | 79 | 77 | 35 | 185 mm² |  | 39 | 42 | 39 | 13 | 185 mm² |  | 14 | 25 | 19 | 16 | [14 empty] | Total Load R: 173; Total Load Y: 146; Total Load B: 135; Total Load N: 64 | 173 | 135 | 24.7507 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN02 | 23.267674, 56.538849 | 252 | Ground (GMT) | 3 | 1000 | 07/06/2026, 13:50 | 1 | 239 | 239 | 241 | 414 | 416 | 419 | [18 empty] | 185 mm² |  | 124 | 101 | 72 | 62 | 185 mm² |  | 105 | 94 | 70 | 63 | 185 mm² |  | 65 | 55 | 51 | 9 | 240 mm² |  | 15 | 26 | 12 | 15 | 240 mm² |  | 47 | 36 | 18 | 30 | 356 | 312 | 223 | 179 | 356 | 223 | 25.5277 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN02 | 23.276305, 56.532117 | 289 | Pole (PMT) | 3 | 315 | 07/06/2026, 13:32 | 1 | 238 | 236 | 238 | 410 | 412 | 413 | 120 mm² |  | 58 | 86 | 58 | 18 | 120 mm² |  | 13 | 2 | 95 | 84 | [32 empty] | Total Load R: 71; Total Load Y: 88; Total Load B: 153; Total Load N: 102 | 153 | 71 | 34.4926 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN02 | 23.273717, 56.527718 | 402 | Pole (PMT) | 3 | 315 | 07/06/2026, 13:26 | 1 | 238 | 237 | 241 | 413 | 416 | 419 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 72 | 56 | 46 | 17 | [32 empty] | Total Load R: 72; Total Load Y: 56; Total Load B: 46; Total Load N: 17 | 72 | 46 | 16.3506 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN02 | 23.27685, 56.528972 | 401 | Ground (GMT) |  | 1000 | 07/06/2026, 13:21 | 1 | 241 | 249 | 242 | 416 | 418 | 422 | 185 mm² | [17 empty] | 185 mm² |  | 17 | 0 | 0 | 14 | 185 mm² |  | 78 | 74 | 42 | 36 | 185 mm² |  | 100 | 46 | 48 | 52 | [8 empty] | Total Load R: 195; Total Load Y: 120; Total Load B: 90; Total Load N: 102 | 195 | 90 | 14.0504 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN02 | 23.317298, 56.615638 | 1800 | Pole (PMT) |  | 315 | 06/06/2026, 13:14 | 1 | 238 | 237 | 240 | 409 | 418 | 413 | 185 mm² |  | 135 | 137 | 145 | 11 | 185 mm² |  | 158 | 56 | 20 | 120 | [32 empty] | Total Load R: 293; Total Load Y: 193; Total Load B: 165; Total Load N: 131 | 293 | 165 | 65.8933 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN02 | 23.273376, 56.531538 | 288 | Pole (PMT) |  | 315 | 06/06/2026, 13:06 | 1 | 239 | 240 | 242 | 413 | 420 | 418 | 120 mm² |  | 107 | 31 | 8 | 80 | 120 mm² |  | 63 | 36 | 95 | 44 | [32 empty] | Total Load R: 170; Total Load Y: 67; Total Load B: 103; Total Load N: 124 | 170 | 67 | 38.6055 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN02 | 23.270033, 56.530315 | 287 | Pole (PMT) |  | 315 | 06/06/2026, 13:00 | 1 | 245 | 244 | 247 | 425 | 428 | 426 | 185 mm² |  | 34 | 95 | 87 | 40 | 120 mm² |  | 114 | 44 | 71 | 48 | [32 empty] | Total Load R: 148; Total Load Y: 139; Total Load B: 158; Total Load N: 88 | 158 | 139 | 36.9229 | OK - No Upgrade | OK - Balanced
Araqi | AL-ARAQI | K_LN02 | 23.266127, 56.522362 | 290 | Pole (PMT) |  | 315 | 06/06/2026, 12:49 | 1 | 240 | 239 | 242 | 414 | 420 | 420 | 120 mm² |  | 113 | 62 | 104 | 52 | [38 empty] | Total Load R: 113; Total Load Y: 62; Total Load B: 104; Total Load N: 52 | 113 | 62 | 25.7234 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN02 | 23.262074, 56.523987 | 4763 | Pole (PMT) |  | 200 | 06/06/2026, 12:43 | 1 | 249 | 251 | 249 | 435 | 430 | 434 | 240 mm² |  | 98 | 115 | 98 | 17 | [38 empty] | Total Load R: 98; Total Load Y: 115; Total Load B: 98; Total Load N: 17 | 115 | 98 | 43.3229 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN02 | 23.260312, 56.522553 | 1696 | Ground (GMT) |  | 1000 | 06/06/2026, 12:38 | 1 | 252 | 251 | 250 | 438 | 437 | 433 | [30 empty] | 185 mm² |  | 140 | 78 | 131 | 55 | 185 mm² |  | 10 | 23 | 20 | 11 | 185 mm² |  | 77 | 32 | 1 | 68 | 227 | 133 | 152 | 134 | 227 | 133 | 17.2211 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN07 | 23.272353, 56.541292 | 2309 | Pole (PMT) |  | 315 | 31/05/2026, 14:54 | 1 | 248 | 247 | 248 | 430 | 430 | 431 | 185 mm² |  | 85 | 67 | 115 | 50 | [38 empty] | Total Load R: 85; Total Load Y: 67; Total Load B: 115; Total Load N: 50 | 115 | 67 | 27.1904 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN07 | 23.279983, 56.543408 | 1318 | Pole (PMT) |  | 315 | 31/05/2026, 14:46 | 1 | 253 | 251 | 250 | 436 | 435 | 434 | 185 mm² |  | 120 | 150 | 218 | 60 | 185 mm² |  | 10 | 25 | 7 | 8 | [32 empty] | Total Load R: 130; Total Load Y: 175; Total Load B: 225; Total Load N: 68 | 225 | 130 | 53.941 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN07 | 23.279921, 56.541241 | 507 | Pole (PMT) |  | 315 | 31/05/2026, 14:42 | 1 | 249 | 248 | 249 | 431 | 430 | 430 | 185 mm² |  | 50 | 65 | 110 | 35 | 185 mm² |  | 20 | 12 | 18 | 5 | [32 empty] | Total Load R: 70; Total Load Y: 77; Total Load B: 128; Total Load N: 40 | 128 | 70 | 30.3345 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN07 | 23.276813, 56.542557 | 390 | Ground (GMT) |  | 1000 | 31/05/2026, 14:38 | 1 | 252 | 251 | 253 | 436 | 437 | 437 | [6 empty] | 185 mm² |  | 30 | 135 | 45 | 88 | 120 mm² |  | 75 | 95 | 135 | 60 | 120 mm² |  | 20 | 31 | 10 | 15 | 120 mm² |  | 95 | 85 | 75 | 25 | 185 mm² |  | 65 | 60 | 80 | 35 | 185 mm² |  | 75 | 95 | 88 | 40 | 185 mm² |  | 110 | 75 | 160 | 93 | 470 | 576 | 593 | 356 | 593 | 470 | 44.7818 | OK - No Upgrade | OK - Balanced
Araqi | AL-ARAQI | K_LN07 | 23.274825, 56.541057 | 391 | Pole (PMT) |  | 315 | 31/05/2026, 14:35 | 1 | 244 | 246 | 246 | 426 | 425 | 427 | 120 mm² |  | 145 | 95 | 151 | 50 | 120 mm² |  | 60 | 40 | 51 | 11 | [32 empty] | Total Load R: 205; Total Load Y: 135; Total Load B: 202; Total Load N: 61 | 205 | 135 | 48.019 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN07 | 23.274604, 56.537937 | 393 | Pole (PMT) |  | 315 | 31/05/2026, 14:30 | 1 | 246 | 245 | 247 | 426 | 427 | 428 | 120 mm² |  | 85 | 115 | 75 | 60 | 120 mm² |  | 87 | 50 | 30 | 16 | [32 empty] | Total Load R: 172; Total Load Y: 165; Total Load B: 105; Total Load N: 76 | 172 | 105 | 40.2892 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN07 | 23.273839, 56.536136 | 1388 | Pole (PMT) |  | 315 | 31/05/2026, 14:29 | 1 | 246 | 246 | 246 | 427 | 428 | 425 | 185 mm² |  | 95 | 35 | 34 | 41 | 185 mm² |  | 67 | 85 | 57 | 12 | [32 empty] | Total Load R: 162; Total Load Y: 120; Total Load B: 91; Total Load N: 53 | 162 | 91 | 38.0358 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN07 | 23.274818, 56.53459 | 394 | Ground (GMT) |  | 1000 | 31/05/2026, 14:25 | 1 | 247 | 248 | 247 | 431 | 426 | 430 | [12 empty] | 120 mm² |  | 0 | 2 | 2 | 2 | 120 mm² |  | 15 | 15 | 0 | 12 | 120 mm² |  | 6 | 17 | 40 | 31 | 120 mm² |  | 3 | 22 | 25 | 20 | 185 mm² |  | 50 | 110 | 105 | 60 | 185 mm² |  | 95 | 90 | 82 | 50 | 169 | 256 | 254 | 175 | 256 | 169 | 19.1108 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN07 | 23.272622, 56.539188 | 392 | Pole (PMT) |  | 315 | 31/05/2026, 14:13 | 1 | 244 | 243 | 245 | 423 | 425 | 422 | 120 mm² |  | 40 | 35 | 37 | 11 | 185 mm² |  | 30 | 75 | 60 | 39 | 185 mm² |  | 35 | 60 | 26 | 21 | [26 empty] | Total Load R: 105; Total Load Y: 170; Total Load B: 123; Total Load N: 71 | 170 | 105 | 39.5402 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN07 | 23.270806, 56.53825 | 250 | Ground (GMT) |  | 1000 | 31/05/2026, 14:08 | 1 | 250 | 250 | 252 | 431 | 432 | 436 | [6 empty] | 185 mm² |  | 6 | 16 | 11 | 7 | 185 mm² |  | 115 | 120 | 66 | 48 | 240 mm² |  | 155 | 135 | 110 | 40 | 185 mm² |  | 50 | 65 | 30 | 21 | 240 mm² |  | 60 | 67 | 50 | 23 | 185 mm² |  | 110 | 70 | 110 | 53 | 240 mm² |  | 90 | 95 | 130 | 40 | 586 | 568 | 507 | 232 | 586 | 507 | 43.7457 | OK - No Upgrade | OK - Balanced
Araqi | AL-ARAQI | K_LN07 | 23.27026, 56.534497 | 248 | Ground (GMT) |  | 1000 | 31/05/2026, 14:02 | 1 | 245 | 242 | 245 | 425 | 425 | 424 | 240 mm² |  | 60 | 89 | 53 | 35 | [6 empty] | 185 mm² |  | 27 | 60 | 65 | 45 | 185 mm² |  | 30 | 115 | 60 | 25 | 185 mm² |  | 71 | 60 | 45 | 20 | 185 mm² |  | 60 | 45 | 110 | 79 | 185 mm² |  | 65 | 118 | 79 | 60 |  |  | Total Load R: 313; Total Load Y: 487; Total Load B: 412; Total Load N: 264 | 487 | 313 | 35.8491 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN07 | 23.269857, 56.534476 | 249 | Ground (GMT) |  | 1000 | 31/05/2026, 13:57 | 1 | 245 | 245 | 247 | 425 | 428 | 427 | [18 empty] | 185 mm² |  | 85 | 88 | 98 | 25 | 185 mm² |  | 135 | 60 | 135 | 85 | 120 mm² |  | 55 | 25 | 35 | 22 | 240 mm² |  | 60 | 40 | 61 | 19 |  |  | Total Load R: 335; Total Load Y: 213; Total Load B: 329; Total Load N: 151 | 335 | 213 | 24.6601 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN07 | 23.267829, 56.535275 | 1860 | Ground (GMT) |  | 1000 | 31/05/2026, 13:52 | 1 | 246 | 248 | 247 | 430 | 429 | 431 | [18 empty] | 185 mm² |  | 110 | 135 | 108 | 35 | 185 mm² |  | 60 | 45 | 10 | 28 | 185 mm² |  | 37 | 35 | 90 | 45 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 0 | 0 | 0 | 0 | 207 | 215 | 208 | 108 | 215 | 207 | 16.0128 | OK - No Upgrade | OK - Balanced
Araqi | AL-ARAQI | K_LN07 | 23.264575, 56.534542 | 2174 | Ground (GMT) |  | 1000 | 31/05/2026, 13:44 | 1 | 247 | 247 | 248 | 426 | 420 | 430 | 185 mm² |  | 30 | 25 | 37 | 18 | 185 mm² |  | 95 | 49 | 146 | 87 | 185 mm² |  | 60 | 48 | 57 | 18 | 185 mm² |  | 60 | 67 | 61 | 21 | [20 empty] | Total Load R: 245; Total Load Y: 189; Total Load B: 301; Total Load N: 144 | 301 | 189 | 22.2094 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN07 | 23.263084, 56.531388 | 246 | Ground (GMT) |  | 1000 | 31/05/2026, 13:39 | 1 | 248 | 249 | 250 | 429 | 433 | 431 | 185 mm² |  | 20 | 11 | 5 | 6 | 185 mm² |  | 45 | 35 | 10 | 17 | 185 mm² |  | 75 | 22 | 110 | 70 | [26 empty] | Total Load R: 140; Total Load Y: 68; Total Load B: 125; Total Load N: 93 | 140 | 68 | 10.4027 | OK - No Upgrade | Need to Balance
Araqi | AL-ARAQI | K_LN07 | 23.261957, 56.52878 | 245 | Ground (GMT) |  | 1000 | 31/05/2026, 13:33 | 1 | 248 | 248 | 250 | 430 | 432 | 431 | 70 mm² |  | 35 | 38 | 37 | 25 | [6 empty] | 120 mm² |  | 151 | 160 | 170 | 65 | 120 mm² |  | 85 | 114 | 120 | 50 | 185 mm² |  | 85 | 45 | 87 | 50 | 185 mm² |  | 85 | 60 | 89 | 27 | [8 empty] | Total Load R: 441; Total Load Y: 417; Total Load B: 503; Total Load N: 217 | 503 | 417 | 37.4625 | OK - No Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN3 | 23.261042, 56.526919 | 914 | Ground (GMT) |  | 500 | 03/05/2026, 12:14 | 1 | 245 | 245 | 246 | 424 | 428 | 428 | 240 mm² |  | 116 | 125 | 96 | 60 | [6 empty] | 240 mm² |  | 85 | 96 | 105 | 43 | [26 empty] | Total Load R: 201; Total Load Y: 221; Total Load B: 201; Total Load N: 103 | 221 | 201 | 32.46 | OK - No Upgrade | OK - Balanced
Ibri | AL-ARAQI | K_LN3 | 23.242605, 56.514059 | 915 | Ground (GMT) | 3 | 500 | 03/05/2026, 12:13 | 1 | 243 | 243 | 245 | 421 | 422 | 423 | [6 empty] | 240 mm² |  | 124 | 90 | 114 | 45 | 240 mm² |  | 100 | 140 | 176 | 65 | [26 empty] | Total Load R: 224; Total Load Y: 230; Total Load B: 290; Total Load N: 110 | 290 | 224 | 42.2932 | OK - No Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN5 |  | 270 | Ground (GMT) |  | 500 | 03/05/2026, 12:10 | 1 | 233 | 232 | 234 | 403 | 405 | 406 | 240 mm² |  | 202 | 135 | 140 | 157 | 240 mm² |  | 128 | 145 | 159 | 153 | [32 empty] | Total Load R: 330; Total Load Y: 280; Total Load B: 299; Total Load N: 310 | 330 | 280 | 46.0691 | OK - No Upgrade | OK - Balanced
Ibri | AL-ARAQI | K_LN5 | 23.204746, 56.470239 | 271 | Ground (GMT) |  | 500 | 03/05/2026, 12:07 | 1 | 244 | 244 | 246 | 423 | 424 | 426 | [12 empty] | 185 mm² |  | 19 | 10 | 3 | 10 | 185 mm² |  | 45 | 41 | 47 | 10 | 120 mm² |  | 50 | 85 | 63 | 13 | [14 empty] | Total Load R: 114; Total Load Y: 136; Total Load B: 113; Total Load N: 33 | 136 | 113 | 19.9283 | OK - No Upgrade | Need to Balance
Ibri | AL-ARAQI | K_LN5 |  | 918 | Ground (GMT) |  | 500 | 03/05/2026, 12:04 | 1 | 243 | 243 | 246 | 422 | 423 | 425 | 240 mm² |  | 144 | 100 | 141 | 28 | 240 mm² |  | 100 | 86 | 106 | 33 | [32 empty] | Total Load R: 244; Total Load Y: 186; Total Load B: 247; Total Load N: 61 | 247 | 186 | 36.1077 | OK - No Upgrade | OK - Balanced
Ibri | AL-ARAQI | K_LN5 |  | 919 | Ground (GMT) |  | 500 | 03/05/2026, 12:02 | 1 | 244 | 245 | 247 | 424 | 427 | 426 | [12 empty] | 240 mm² |  | 103 | 90 | 85 | 108 | 240 mm² |  | 91 | 87 | 70 | 116 | [20 empty] | Total Load R: 194; Total Load Y: 177; Total Load B: 155; Total Load N: 224 | 194 | 155 | 28.4943 | OK - No Upgrade | Need to Balance

## AL-SANAEYYAH
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Ibri | AL-SANAEYYAH | K_LN13 | 23.217267, 56.482271 | 1909 | Ground (GMT) |  | 1000 | 31/05/2026, 20:50 | 1 | 247 | 246 | 250 | 426 | 433 | 432 | 185 mm² |  | 61 | 31 | 29 | 24 | 185 mm² |  | 116 | 42 | 94 | 73 | 185 mm² |  | 24 | 14 | 25 | 20 | 185 mm² |  | 20 | 31 | 3 | 26 | 240 mm² |  | 25 | 22 | 40 | 27 | 240 mm² |  | 38 | 51 | 24 | 40 | [6 empty] | 240 mm² |  | 8 | 1 | 1 | 4 | 292 | 192 | 216 | 214 | 292 | 192 | 21.5453 | OK - No Upgrade | Need to Balance
Ibri | AL-SANAEYYAH | K_LN6 | 23.253655, 56.487771 | 4758 | Ground (GMT) |  | 1000 | 10/05/2026, 13:10 | 1 | 247 | 248 | 251 | 429 | 434 | 435 | 300 mm² |  | 2 | 11 | 5 | 9 | 300 mm² |  | 84 | 5 | 11 | 1 | 300 mm² |  | 1 | 1 | 1 | 2 | 300 mm² |  | 7 | 4 | 2 | 3 | 300 mm² |  | 14 | 8 | 1 | 10 | [12 empty] | 120 mm² |  | 0 | 1 | 1 | 0 | 108 | 30 | 21 | 25 | 108 | 21 | 8.0249 | OK - No Upgrade | Need to Balance
Ibri | AL-SANAEYYAH | K_LN17 | 23.251928, 56.488603 | 4757 | Ground (GMT) |  | 1000 | 06/05/2026, 20:51 | 1 | 237 | 239 | 242 | 410 | 419 | 419 | [6 empty] | 240 mm² |  | 137 | 100 | 62 | 58 | 240 mm² |  | 37 | 73 | 84 | 23 | 240 mm² |  | 94 | 37 | 30 | 68 | 240 mm² |  | 112 | 66 | 55 | 61 | 240 mm² |  | 115 | 32 | 26 | 30 | 240 mm² |  | 113 | 74 | 37 | 60 | 120 mm² |  | 75 | 50 | 70 | 20 | 683 | 432 | 364 | 320 | 683 | 364 | 48.5026 | OK - No Upgrade | Need to Balance
Ibri | AL-SANAEYYAH | K_LN17 | 23.251928, 56.488603 | 4757 | Ground (GMT) |  | 1000 | 13/05/2026, 10:37 | 2 | 240 | 241 | 243 | 415 | 423 | 422 | [6 empty] | 240 mm² |  | 163 | 104 | 94 | 74 | 240 mm² |  | 101 | 70 | 69 | 25 | 240 mm² |  | 92 | 58 | 53 | 45 | 240 mm² |  | 100 | 53 | 50 | 49 | 240 mm² |  | 124 | 35 | 28 | 20 | 120 mm² |  | 104 | 74 | 38 | 46 |  |  | 71 | 35 | 67 | 44 | 755 | 429 | 399 | 303 | 755 | 399 | 54.2695 | OK - No Upgrade | Need to Balance
Ibri | AL-SANAEYYAH | K_LN17 | 23.251943, 56.488569 | 86 | Ground (GMT) |  | 1000 | 06/05/2026, 12:33 | 1 | 238 | 238 | 242 | 410 | 418 | 418 | [6 empty] | 185 mm² |  | 76 | 31 | 44 | 37 | 185 mm² |  | 153 | 131 | 136 | 41 | [26 empty] | Total Load R: 229; Total Load Y: 162; Total Load B: 180; Total Load N: 78 | 229 | 162 | 16.2622 | OK - No Upgrade | Need to Balance
Ibri | AL-SANAEYYAH | K_LN17 | 23.251943, 56.488569 | 86 | Ground (GMT) |  | 1000 | 10/05/2026, 11:38 | 2 | 240 | 241 | 243 | 417 | 421 | 421 | 185 mm² |  | 75 | 37 | 63 | 31 | 185 mm² |  | 136 | 112 | 114 | 42 | [32 empty] | Total Load R: 211; Total Load Y: 149; Total Load B: 177; Total Load N: 73 | 211 | 149 | 15.2398 | OK - No Upgrade | Need to Balance
Ibri | AL-SANAEYYAH | K_LN9 |  | 56 | Ground (GMT) |  | 1000 | 04/05/2026, 09:08 | 1 | 245 | 245 | 248 | 425 | 430 | 428 | [6 empty] | 120 mm² |  | 3 | 16 | 1 | 16 | [32 empty] | Total Load R: 3; Total Load Y: 16; Total Load B: 1; Total Load N: 16 | 16 | 1 | 1.1778 | OK - No Upgrade | Need to Balance
Ibri | AL-SANAEYYAH | K_LN2 |  | 1972 | Ground (GMT) |  | 1000 | 04/05/2026, 09:00 | 1 | 243 | 246 | 244 | 425 | 422 | 428 | 630 mm² |  | 150 | 86 | 126 | 98 | [38 empty] | Total Load R: 150; Total Load Y: 86; Total Load B: 126; Total Load N: 98 | 150 | 86 | 11.0418 | OK - No Upgrade | Need to Balance

## Hamra AlDaroo
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.682583, 56.540912 | 31 | Pole (PMT) |  | 100 | 21/05/2026, 09:20 | 1 | 242 | 241 | 241 | 423 | 422 | 422 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.694864, 56.583987 | 11 | Pole (PMT) |  | 100 | 21/05/2026, 09:08 | 1 | 242 | 242 | 241 | 421 | 420 | 421 | 70 mm² |  | 10 | 10 | 10 | 0 | [38 empty] | Total Load R: 10; Total Load Y: 10; Total Load B: 10; Total Load N: 0 | 10 | 10 | 7.2919 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.835796, 56.658766 | 46 | Pole (PMT) |  | 100 | 21/05/2026, 06:44 | 1 | 238 | 234 | 235 | 413 | 406 | 411 | 120 mm² |  | 0 | 2 | 1 | 1 | [38 empty] | Total Load R: 0; Total Load Y: 2; Total Load B: 1; Total Load N: 1 | 2 | 0 | 1.4307 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.817537, 56.73096 | 51 | Pole (PMT) |  | 100 | 20/05/2026, 15:44 | 1 | 240 | 243 | 240 | 421 | 413 | 419 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.841258, 56.755425 | 51 | Pole (PMT) |  | 100 | 20/05/2026, 14:57 | 1 | 233 | 237 | 235 | 410 | 405 | 409 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.841258, 56.755425 | 66 | Pole (PMT) |  | 100 | 21/05/2026, 06:46 | 1 | 243 | 248 | 243 | 428 | 420 | 427 | 120 mm² |  | 27 | 21 | 24 | 5 | [38 empty] | Total Load R: 27; Total Load Y: 21; Total Load B: 24; Total Load N: 5 | 27 | 21 | 20.0156 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.83978, 56.754737 | 50 | Pole (PMT) |  | 100 | 20/05/2026, 14:39 | 1 | 242 | 248 | 246 | 428 | 424 | 428 | 120 mm² |  | 13 | 0 | 0 | 12 | 120 mm² |  | 23 | 12 | 10 | 13 | [32 empty] | Total Load R: 36; Total Load Y: 12; Total Load B: 10; Total Load N: 25 | 36 | 10 | 26.6874 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.841258, 56.755425 | 49 | Pole (PMT) |  | 100 | 20/05/2026, 14:39 | 1 | 233 | 237 | 234 | 410 | 404 | 409 | 70 mm² |  | 2 | 1 | 2 | 0 | [38 empty] | Total Load R: 2; Total Load Y: 1; Total Load B: 2; Total Load N: 0 | 2 | 1 | 1.4203 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.816189, 56.736889 | 48 | Pole (PMT) |  | 100 | 21/05/2026, 06:47 | 1 | 240 | 244 | 241 | 422 | 415 | 422 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.816167, 56.736884 | 45 | Pole (PMT) |  | 100 | 20/05/2026, 14:20 | 1 | 234 | 238 | 234 | 412 | 411 | 410 | 120 mm² |  | 0 | 0 | 12 | 12 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 12; Total Load N: 12 | 12 | 0 | 8.5633 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.760884, 56.681434 | 17 | Pole (PMT) |  | 100 | 19/05/2026, 11:28 | 1 | 233 | 233 | 232 | 405 | 403 | 404 | 120 mm² |  | 20 | 15 | 14 | 8 | [38 empty] | Total Load R: 20; Total Load Y: 15; Total Load B: 14; Total Load N: 8 | 20 | 14 | 14.0296 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.76088, 56.681479 | 44 | Pole (PMT) |  | 100 | 19/05/2026, 11:27 | 1 | 234 | 235 | 232 | 408 | 405 | 406 | 120 mm² |  | 1 | 3 | 17 | 15 | [38 empty] | Total Load R: 1; Total Load Y: 3; Total Load B: 17; Total Load N: 15 | 17 | 1 | 12.0135 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.768301, 56.677723 | 40 | Pole (PMT) |  | 100 | 19/05/2026, 11:25 | 1 | 233 | 234 | 232 | 408 | 404 | 406 | 240 mm² |  | 1 | 1 | 1 | 1 | [46 empty] | 1 | 1 | 0.70668 | OK - No Upgrade | OK - Balanced | bar: Total Load R to Total Load N
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.777766, 56.678499 | 64 | Pole (PMT) |  | 100 | 19/05/2026, 11:24 | 1 | 234 | 234 | 233 | 408 | 405 | 404 | 120 mm² |  | 1 | 1 | 1 | 1 | [46 empty] | 1 | 1 | 0.70668 | OK - No Upgrade | OK - Balanced | bar: Total Load R to Total Load N
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.777031, 56.680473 | 39 | Pole (PMT) |  | 100 | 20/05/2026, 13:46 | 1 | 233 | 233 | 232 | 407 | 404 | 403 | 120 mm² |  | 1 | 1 | 1 | 1 | [46 empty] | 1 | 1 | 0.70494 | OK - No Upgrade | OK - Balanced | bar: Total Load R to Total Load N
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.769454, 56.677387 | 41 | Pole (PMT) |  | 100 | 19/05/2026, 11:17 | 1 | 232 | 231 | 230 | 404 | 402 | 401 | 120 mm² |  | 1 | 1 | 1 | 1 | [46 empty] | 1 | 1 | 0.69975 | OK - No Upgrade | OK - Balanced | bar: Total Load R to Total Load N
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.760852, 56.681442 | 42 | Pole (PMT) |  | 100 | 19/05/2026, 11:16 | 1 | 233 | 233 | 231 | 405 | 403 | 404 | 120 mm² |  | 25 | 26 | 35 | 8 | [38 empty] | Total Load R: 25; Total Load Y: 26; Total Load B: 35; Total Load N: 8 | 35 | 25 | 24.5518 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 38 | Pole (PMT) |  | 100 | 19/05/2026, 11:14 | 1 | 233 | 235 | 233 | 410 | 405 | 405 | 120 mm² |  | 5 | 1 | 1 | 1 | [38 empty] | Total Load R: 5; Total Load Y: 1; Total Load B: 1; Total Load N: 1 | 5 | 1 | 3.5507 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 36 | Pole (PMT) |  | 100 | 19/05/2026, 11:12 | 1 | 232 | 231 | 230 | 401 | 402 | 401 | 120 mm² |  | 1 | 1 | 1 | 1 | [46 empty] | 1 | 1 | 0.69455 | OK - No Upgrade | OK - Balanced | bar: Total Load R to Total Load N
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 37 | Pole (PMT) |  | 100 | 19/05/2026, 11:10 | 1 | 236 | 237 | 235 | 410 | 408 | 410 | 120 mm² |  | 76 | 63 | 85 | 28 | [38 empty] | Total Load R: 76; Total Load Y: 63; Total Load B: 85; Total Load N: 28 | 85 | 63 | 60.362 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 35 | Pole (PMT) |  | 100 | 19/05/2026, 11:09 | 1 | 242 | 243 | 241 | 419 | 420 | 422 | 120 mm² |  | 1 | 1 | 2 | 1 | [38 empty] | Total Load R: 1; Total Load Y: 1; Total Load B: 2; Total Load N: 1 | 2 | 1 | 1.4515 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.727664, 56.618678 | 5 | Pole (PMT) |  | 100 | 19/05/2026, 10:30 | 1 | 234 | 234 | 233 | 405 | 404 | 404 | 70 mm² |  | 8 | 5 | 15 | 8 | 120 mm² |  | 1 | 1 | 15 | 10 | [32 empty] | Total Load R: 9; Total Load Y: 6; Total Load B: 30; Total Load N: 18 | 30 | 6 | 21.0444 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.737527, 56.615724 | 6 | Pole (PMT) |  | 100 | 19/05/2026, 10:17 | 1 | 232 | 231 | 232 | 401 | 403 | 401 | 120 mm² |  | 32 | 32 | 13 | 17 | [38 empty] | Total Load R: 32; Total Load Y: 32; Total Load B: 13; Total Load N: 17 | 32 | 13 | 22.2257 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.742113, 56.605665 | 57 | Pole (PMT) |  | 100 | 19/05/2026, 10:11 | 1 | 245 | 244 | 243 | 422 | 422 | 421 | 120 mm² |  | 2 | 2 | 1 | 2 | [38 empty] | Total Load R: 2; Total Load Y: 2; Total Load B: 1; Total Load N: 2 | 2 | 1 | 1.4619 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.754879, 56.604276 | 9 | Pole (PMT) |  | 100 | 19/05/2026, 10:06 | 1 | 243 | 242 | 242 | 420 | 419 | 419 | 120 mm² |  | 2 | 2 | 1 | 0 | [38 empty] | Total Load R: 2; Total Load Y: 2; Total Load B: 1; Total Load N: 0 | 2 | 1 | 1.4549 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.751807, 56.604558 | 7 | Pole (PMT) |  | 100 | 19/05/2026, 09:59 | 1 | 243 | 242 | 243 | 420 | 420 | 419 | 120 mm² |  | 3 | 1 | 0 | 0 | [38 empty] | Total Load R: 3; Total Load Y: 1; Total Load B: 0; Total Load N: 0 | 3 | 0 | 2.1824 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.758028, 56.612911 | 8 | Pole (PMT) |  | 100 | 19/05/2026, 09:52 | 1 | 242 | 241 | 241 | 419 | 418 | 419 | 120 mm² |  | 8 | 7 | 10 | 5 | [38 empty] | Total Load R: 8; Total Load Y: 7; Total Load B: 10; Total Load N: 5 | 10 | 7 | 7.2573 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.776837, 56.601989 | 10 | Pole (PMT) |  | 100 | 19/05/2026, 09:46 | 1 | 236 | 237 | 237 | 410 | 413 | 411 | 120 mm² |  | 4 | 43 | 21 | 32 | [38 empty] | Total Load R: 4; Total Load Y: 43; Total Load B: 21; Total Load N: 32 | 43 | 4 | 30.5361 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.908289, 56.622093 | 25 | Pole (PMT) |  | 100 | 19/05/2026, 09:25 | 1 | 236 | 237 | 235 | 402 | 407 | 409 | 120 mm² |  | 83 | 87 | 85 | 4 | [38 empty] | Total Load R: 83; Total Load Y: 87; Total Load B: 85; Total Load N: 4 | 87 | 83 | 60.5767 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.908289, 56.622093 | 25 | Pole (PMT) | 3 | 100 | 11/06/2026, 08:07 | 2 | 250 | 252 | 249 | 435 | 432 | 431 | 120 mm² |  | 27 | 30 | 31 | 15 | [38 empty] | Total Load R: 27; Total Load Y: 30; Total Load B: 31; Total Load N: 15 | 31 | 27 | 23.3567 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.910367, 56.627459 | 26 | Pole (PMT) |  | 200 | 19/05/2026, 09:21 | 1 | 224 | 226 | 225 | 401 | 403 | 401 | 120 mm² |  | 148 | 127 | 112 | 22 | 120 mm² |  | 41 | 29 | 23 | 17 | [32 empty] | Total Load R: 189; Total Load Y: 156; Total Load B: 135; Total Load N: 39 | 189 | 135 | 65.6352 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.910367, 56.627459 | 26 | Pole (PMT) | 03 | 200 | 06/06/2026, 14:05 | 2 | 221 | 227 | 224 | 381 | 394 | 381 | 120 mm² |  | 245 | 118 | 128 | 83 | 120 mm² |  | 31 | 30 | 27 | 8 | [32 empty] | Total Load R: 276; Total Load Y: 148; Total Load B: 155; Total Load N: 91 | 276 | 148 | 91.0678 | Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.90465, 56.629781 | 27 | Pole (PMT) |  | 315 | 19/05/2026, 09:15 | 1 | 238 | 241 | 239 | 414 | 413 | 412 | 120 mm² |  | 107 | 99 | 87 | 17 | 120 mm² |  | 2 | 1 | 7 | 8 | [32 empty] | Total Load R: 109; Total Load Y: 100; Total Load B: 94; Total Load N: 25 | 109 | 94 | 24.8129 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.90465, 56.629781 | 27 | Pole (PMT) | 3 | 315 | 11/06/2026, 08:03 | 2 | 250 | 251 | 249 | 428 | 431 | 429 | 120 mm² |  | 78 | 77 | 74 | 7 | 120 mm² |  | 1 | 1 | 8 | 8 | [32 empty] | Total Load R: 79; Total Load Y: 78; Total Load B: 82; Total Load N: 15 | 82 | 78 | 19.2978 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.901805, 56.624444 | 24 | Pole (PMT) |  | 100 | 19/05/2026, 09:10 | 1 | 231 | 230 | 230 | 400 | 401 | 400 | 120 mm² |  | 19 | 7 | 3 | 13 | [38 empty] | Total Load R: 19; Total Load Y: 7; Total Load B: 3; Total Load N: 13 | 19 | 3 | 13.1636 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.901805, 56.624444 | 24 | Pole (PMT) | 3 | 100 | 11/06/2026, 08:12 | 2 | 240 | 240 | 239 | 416 | 414 | 413 | 120 mm² |  | 8 | 6 | 4 | 3 | [38 empty] | Total Load R: 8; Total Load Y: 6; Total Load B: 4; Total Load N: 3 | 8 | 4 | 5.7643 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.903386, 56.620179 | 23 | Pole (PMT) |  | 100 | 19/05/2026, 09:05 | 1 | 229 | 239 | 229 | 401 | 402 | 401 | 120 mm² |  | 21 | 14 | 13 | 6 | [38 empty] | Total Load R: 21; Total Load Y: 14; Total Load B: 13; Total Load N: 6 | 21 | 13 | 14.5856 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.903386, 56.620179 | 23 | Pole (PMT) | 3 | 100 | 11/06/2026, 08:17 | 2 | 238 | 239 | 235 | 413 | 412 | 409 | 120 mm² |  | 20 | 10 | 20 | 7 | [38 empty] | Total Load R: 20; Total Load Y: 10; Total Load B: 20; Total Load N: 7 | 20 | 10 | 14.3067 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.897989, 56.616751 | 22 | Pole (PMT) |  | 100 | 19/05/2026, 09:02 | 1 | 231 | 232 | 230 | 400 | 401 | 400 | 120 mm² |  | 4 | 8 | 10 | 5 | [38 empty] | Total Load R: 4; Total Load Y: 8; Total Load B: 10; Total Load N: 5 | 10 | 4 | 6.9282 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.897237, 56.611992 | 21 | Pole (PMT) |  | 100 | 19/05/2026, 08:57 | 1 | 235 | 236 | 235 | 408 | 405 | 407 | 120 mm² |  | 33 | 32 | 30 | 5 | [38 empty] | Total Load R: 33; Total Load Y: 32; Total Load B: 30; Total Load N: 5 | 33 | 30 | 23.3203 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.891811, 56.606618 | 20 | Pole (PMT) |  | 315 | 19/05/2026, 08:54 | 1 | 238 | 239 | 238 | 412 | 411 | 409 | 120 mm² |  | 47 | 26 | 32 | 13 | [38 empty] | Total Load R: 47; Total Load Y: 26; Total Load B: 32; Total Load N: 13 | 47 | 26 | 10.6474 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.888711, 56.603389 | 60 | Pole (PMT) |  | 100 | 19/05/2026, 08:50 | 1 | 233 | 234 | 233 | 404 | 402 | 404 | 185 mm² |  | 2 | 1 | 1 | 0 | [38 empty] | Total Load R: 2; Total Load Y: 1; Total Load B: 1; Total Load N: 0 | 2 | 1 | 1.3995 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.868308, 56.599402 | 19 | Pole (PMT) |  | 100 | 19/05/2026, 08:44 | 1 | 232 | 232 | 234 | 401 | 403 | 403 | 120 mm² |  | 16 | 16 | 17 | 4 | [38 empty] | Total Load R: 16; Total Load Y: 16; Total Load B: 17; Total Load N: 4 | 17 | 16 | 11.8074 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.862837, 56.599136 | 18 | Pole (PMT) |  | 200 | 19/05/2026, 08:40 | 1 | 238 | 239 | 237 | 413 | 410 | 411 | 120 mm² |  | 77 | 87 | 76 | 13 | [38 empty] | Total Load R: 77; Total Load Y: 87; Total Load B: 76; Total Load N: 13 | 87 | 76 | 31.1172 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.863451, 56.605195 | 17 | Pole (PMT) |  | 100 | 19/05/2026, 08:35 | 1 | 234 | 235 | 232 | 406 | 403 | 405 | 120 mm² |  | 8 | 7 | 16 | 4 | [38 empty] | Total Load R: 8; Total Load Y: 7; Total Load B: 16; Total Load N: 4 | 16 | 7 | 11.2514 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.853655, 56.603271 | 16 | Pole (PMT) |  | 315 | 19/05/2026, 08:30 | 1 | 245 | 247 | 245 | 426 | 423 | 426 | 120 mm² |  | 67 | 59 | 80 | 17 | [38 empty] | Total Load R: 67; Total Load Y: 59; Total Load B: 80; Total Load N: 17 | 80 | 59 | 18.7391 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.84356, 56.610479 | 15 | Pole (PMT) |  | 100 | 19/05/2026, 08:24 | 1 | 234 | 234 | 234 | 406 | 405 | 403 | 120 mm² |  | 31 | 36 | 43 | 10 | [38 empty] | Total Load R: 31; Total Load Y: 36; Total Load B: 43; Total Load N: 10 | 43 | 31 | 30.2381 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.832136, 56.607543 | 14 | Pole (PMT) |  | 100 | 19/05/2026, 08:17 | 1 | 237 | 238 | 236 | 411 | 409 | 410 | 120 mm² |  | 1 | 1 | 0 | 0 | [38 empty] | Total Load R: 1; Total Load Y: 1; Total Load B: 0; Total Load N: 0 | 1 | 0 | 0.71187 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.83077, 56.598354 | 13 | Pole (PMT) |  | 200 | 19/05/2026, 08:11 | 1 | 249 | 248 | 248 | 426 | 429 | 429 | 120 mm² |  | 45 | 58 | 50 | 14 | [38 empty] | Total Load R: 45; Total Load Y: 58; Total Load B: 50; Total Load N: 14 | 58 | 45 | 21.3978 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.807395, 56.607101 | 12 | Pole (PMT) |  | 315 | 19/05/2026, 08:02 | 1 | 237 | 238 | 236 | 411 | 409 | 410 | 185 mm² |  | 55 | 55 | 55 | 5 | 185 mm² |  | 77 | 58 | 56 | 16 | [32 empty] | Total Load R: 132; Total Load Y: 113; Total Load B: 111; Total Load N: 21 | 132 | 111 | 29.8309 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.807395, 56.607101 | 12 | Pole (PMT) | 3 | 315 | 11/06/2026, 06:52 | 2 | 246 | 246 | 245 | 426 | 424 | 425 | 120 mm² |  | 78 | 76 | 78 | 5 | 120 mm² |  | 64 | 63 | 55 | 5 | [32 empty] | Total Load R: 142; Total Load Y: 139; Total Load B: 133; Total Load N: 10 | 142 | 133 | 33.262 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.791257, 56.610425 | 11 | Pole (PMT) |  | 100 | 19/05/2026, 08:00 | 1 | 232 | 234 | 233 | 401 | 403 | 401 | 120 mm² |  | 121 | 136 | 218 | 63 | [38 empty] | Total Load R: 121; Total Load Y: 136; Total Load B: 218; Total Load N: 63 | 218 | 121 | 151.4124 | Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.791257, 56.610425 | 11 | Pole (PMT) | 3 | 100 | 11/06/2026, 06:46 | 2 | 243 | 242 | 244 | 420 | 421 | 419 | 120 mm² |  | 100 | 71 | 53 | 45 | [38 empty] | Total Load R: 100; Total Load Y: 71; Total Load B: 53; Total Load N: 45 | 100 | 53 | 72.7461 | Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.718493, 56.663778 | 68 | Pole (PMT) |  | 100 | 18/05/2026, 10:12 | 1 | 245 | 246 | 246 | 428 | 426 | 428 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.727601, 56.678467 | 43 | Pole (PMT) |  | 200 | 18/05/2026, 11:32 | 1 | 238 | 239 | 238 | 415 | 413 | 411 | 120 mm² |  | 11 | 19 | 10 | 7 | [38 empty] | Total Load R: 11; Total Load Y: 19; Total Load B: 10; Total Load N: 7 | 19 | 10 | 6.8286 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.73086, 56.692988 | 52 | Pole (PMT) |  | 100 | 17/05/2026, 11:53 | 1 | 238 | 239 | 238 | 415 | 414 | 414 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.737075, 56.701147 | 67 | Pole (PMT) |  | 100 | 17/05/2026, 11:52 | 1 | 238 | 239 | 239 | 415 | 415 | 414 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.738361, 56.700182 | 53 | Pole (PMT) |  | 100 | 17/05/2026, 13:43 | 1 | 250 | 250 | 248 | 436 | 431 | 432 | 120 mm² |  | 12 | 18 | 24 | 12 | [38 empty] | Total Load R: 12; Total Load Y: 18; Total Load B: 24; Total Load N: 12 | 24 | 12 | 18.1242 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.949667, 56.688988 | 31 | Pole (PMT) |  | 200 | 17/05/2026, 11:41 | 1 | 232 | 233 | 231 | 403 | 401 | 403 | 120 mm² |  | 17 | 58 | 17 | 41 | [38 empty] | Total Load R: 17; Total Load Y: 58; Total Load B: 17; Total Load N: 41 | 58 | 17 | 20.2425 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.949774, 56.676685 | 30 | Pole (PMT) |  | 315 | 17/05/2026, 11:37 | 1 | 238 | 241 | 238 | 415 | 411 | 416 | 120 mm² |  | 8 | 5 | 1 | 9 | 120 mm² |  | 28 | 4 | 7 | 28 | [32 empty] | Total Load R: 36; Total Load Y: 9; Total Load B: 8; Total Load N: 37 | 36 | 8 | 8.2149 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.958897, 56.676007 | 42 | Pole (PMT) |  | 100 | 17/05/2026, 11:32 | 1 | 225 | 229 | 226 | 404 | 403 | 404 | 120 mm² |  | 14 | 1 | 14 | 14 | [38 empty] | Total Load R: 14; Total Load Y: 1; Total Load B: 14; Total Load N: 14 | 14 | 1 | 9.7965 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.656639, 56.844153 | 59 | Pole (PMT) |  | 100 | 17/05/2026, 11:26 | 1 | 237 | 237 | 236 | 412 | 412 | 410 | 240 mm² |  | 30 | 23 | 46 | 21 | [38 empty] | Total Load R: 30; Total Load Y: 23; Total Load B: 46; Total Load N: 21 | 46 | 23 | 32.8258 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.966059, 56.680735 | 43 | Pole (PMT) |  | 200 | 17/05/2026, 13:44 | 1 | 233 | 234 | 232 | 405 | 401 | 403 | 120 mm² |  | 1 | 1 | 13 | 13 | [38 empty] | Total Load R: 1; Total Load Y: 1; Total Load B: 13; Total Load N: 13 | 13 | 1 | 4.5596 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.656673, 56.844097 | 63 | Pole (PMT) |  | 100 | 17/05/2026, 11:24 | 1 | 233 | 234 | 233 | 408 | 405 | 407 | 120 mm² |  | 0 | 1 | 2 | 2 | [38 empty] | Total Load R: 0; Total Load Y: 1; Total Load B: 2; Total Load N: 2 | 2 | 0 | 1.4134 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.656627, 56.844302 | 58 | Pole (PMT) |  | 100 | 17/05/2026, 11:23 | 1 | 233 | 232 | 233 | 405 | 406 | 408 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.656659, 56.844268 | 57 | Pole (PMT) |  | 100 | 17/05/2026, 11:22 | 1 | 240 | 239 | 238 | 415 | 415 | 414 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.973507, 56.68488 | 44 | Pole (PMT) |  | 50 | 17/05/2026, 11:21 | 1 | 227 | 228 | 225 | 404 | 403 | 404 | 120 mm² |  | 2 | 2 | 15 | 14 | [38 empty] | Total Load R: 2; Total Load Y: 2; Total Load B: 15; Total Load N: 14 | 15 | 2 | 20.9925 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.656621, 56.844156 | 56 | Pole (PMT) |  | 100 | 17/05/2026, 11:20 | 1 | 236 | 238 | 237 | 412 | 411 | 411 | 120 mm² |  | 39 | 20 | 18 | 18 | [38 empty] | Total Load R: 39; Total Load Y: 20; Total Load B: 18; Total Load N: 18 | 39 | 18 | 27.8306 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.656616, 56.844066 | 65 | Pole (PMT) |  | 100 | 17/05/2026, 11:18 | 1 | 238 | 238 | 237 | 414 | 413 | 413 | 120 mm² |  | 10 | 10 | 10 | 1 | [38 empty] | Total Load R: 10; Total Load Y: 10; Total Load B: 10; Total Load N: 1 | 10 | 10 | 7.1707 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.6593, 56.844269 | 60 | Pole (PMT) |  | 100 | 18/05/2026, 11:35 | 1 | 239 | 239 | 238 | 416 | 414 | 414 | 120 mm² |  | 1 | 1 | 2 | 2 | [38 empty] | Total Load R: 1; Total Load Y: 1; Total Load B: 2; Total Load N: 2 | 2 | 1 | 1.4411 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.659258, 56.844289 | 55 | Pole (PMT) |  | 100 | 17/05/2026, 11:14 | 1 | 237 | 237 | 236 | 412 | 411 | 412 | 120 mm² |  | 28 | 27 | 26 | 1 | [38 empty] | Total Load R: 28; Total Load Y: 27; Total Load B: 26; Total Load N: 1 | 28 | 26 | 19.9809 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.667275, 56.843648 | 54 | Pole (PMT) |  | 100 | 18/05/2026, 11:33 | 1 | 243 | 242 | 243 | 421 | 419 | 418 | 120 mm² |  | 30 | 20 | 22 | 10 | [38 empty] | Total Load R: 30; Total Load Y: 20; Total Load B: 22; Total Load N: 10 | 30 | 20 | 21.8758 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.964262, 56.727778 | 32 | Pole (PMT) |  | 100 | 17/05/2026, 11:10 | 1 | 227 | 229 | 227 | 404 | 403 | 403 | 120 mm² |  | 1 | 1 | 1 | 0 | [38 empty] | Total Load R: 1; Total Load Y: 1; Total Load B: 1; Total Load N: 0 | 1 | 1 | 0.69975 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.959873, 56.750506 | 33 | Pole (PMT) |  | 100 | 17/05/2026, 11:02 | 1 | 238 | 240 | 238 | 413 | 411 | 413 | 120 mm² |  | 3 | 1 | 4 | 1 | [38 empty] | Total Load R: 3; Total Load Y: 1; Total Load B: 4; Total Load N: 1 | 4 | 1 | 2.8613 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.954167, 56.776297 | 36 | Pole (PMT) |  | 100 | 17/05/2026, 10:54 | 1 | 236 | 239 | 238 | 411 | 409 | 413 | 120 mm² |  | 16 | 5 | 4 | 13 | [38 empty] | Total Load R: 16; Total Load Y: 5; Total Load B: 4; Total Load N: 13 | 16 | 4 | 11.39 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.957876, 56.758019 | 35 | Pole (PMT) |  | 100 | 17/05/2026, 10:46 | 1 | 226 | 228 | 226 | 401 | 403 | 402 | 120 mm² |  | 1 | 1 | 1 | 1 | [46 empty] | 1 | 1 | 0.69455 | OK - No Upgrade | OK - Balanced | bar: Total Load R to Total Load N
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 23.000484, 56.745537 | 34 | Pole (PMT) |  | 100 | 17/05/2026, 10:35 | 1 | 226 | 228 | 226 | 404 | 403 | 404 | 120 mm² |  | 3 | 2 | 1 | 1 | [38 empty] | Total Load R: 3; Total Load Y: 2; Total Load B: 1; Total Load N: 1 | 3 | 1 | 2.0992 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 23.024832, 56.692345 | 46 | Pole (PMT) |  | 100 | 17/05/2026, 10:20 | 1 | 238 | 240 | 239 | 413 | 410 | 412 | 120 mm² |  | 2 | 1 | 1 | 0 | [38 empty] | Total Load R: 2; Total Load Y: 1; Total Load B: 1; Total Load N: 0 | 2 | 1 | 1.4307 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 23.027362, 56.686526 | 59 | Pole (PMT) |  | 100 | 17/05/2026, 10:15 | 1 | 226 | 227 | 225 | 402 | 401 | 402 | 120 mm² |  | 2 | 1 | 1 | 13 | [38 empty] | Total Load R: 2; Total Load Y: 1; Total Load B: 1; Total Load N: 13 | 2 | 1 | 1.3926 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 23.031104, 56.688251 | 47 | Pole (PMT) |  | 100 | 17/05/2026, 10:12 | 1 | 226 | 228 | 225 | 402 | 403 | 402 | 120 mm² |  | 1 | 1 | 10 | 5 | [38 empty] | Total Load R: 1; Total Load Y: 1; Total Load B: 10; Total Load N: 5 | 10 | 1 | 6.9628 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 23.08051, 56.671661 | 52 | Pole (PMT) |  | 100 | 17/05/2026, 09:59 | 1 | 226 | 221 | 225 | 401 | 402 | 401 | 120 mm² |  | 2 | 1 | 1 | 0 |  |  | 1 | 1 | 17 | 14 | [32 empty] | Total Load R: 3; Total Load Y: 2; Total Load B: 18; Total Load N: 14 | 18 | 2 | 12.5019 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 23.058321, 56.655912 | 51 | Pole (PMT) |  | 100 | 17/05/2026, 09:50 | 1 | 231 | 234 | 232 | 402 | 401 | 402 | 120 mm² |  | 30 | 12 | 4 | 26 | [38 empty] | Total Load R: 30; Total Load Y: 12; Total Load B: 4; Total Load N: 26 | 30 | 4 | 20.8885 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 23.096349, 56.623273 | 54 | Pole (PMT) |  | 100 | 17/05/2026, 09:34 | 1 | 227 | 228 | 226 | 401 | 402 | 401 | 120 mm² |  | 2 | 2 | 3 | 0 | [38 empty] | Total Load R: 2; Total Load Y: 2; Total Load B: 3; Total Load N: 0 | 3 | 2 | 2.0837 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 55 | Pole (PMT) |  | 100 | 17/05/2026, 09:20 | 1 | 227 | 228 | 226 | 402 | 401 | 402 | 120 mm² |  | 2 | 1 | 1 | 0 | [38 empty] | Total Load R: 2; Total Load Y: 1; Total Load B: 1; Total Load N: 0 | 2 | 1 | 1.3926 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 53 | Pole (PMT) |  | 100 | 17/05/2026, 09:13 | 1 | 227 | 228 | 227 | 404 | 402 | 402 | 120 mm² |  | 2 | 1 | 1 | 0 | [38 empty] | Total Load R: 2; Total Load Y: 1; Total Load B: 1; Total Load N: 0 | 2 | 1 | 1.3995 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 50 | Pole (PMT) |  | 200 | 17/05/2026, 09:05 | 1 | 239 | 238 | 237 | 414 | 411 | 410 | 120 mm² |  | 60 | 61 | 45 | 10 | [38 empty] | Total Load R: 60; Total Load Y: 61; Total Load B: 45; Total Load N: 10 | 61 | 45 | 21.8706 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 49 | Pole (PMT) |  | 100 | 17/05/2026, 08:56 | 1 | 229 | 228 | 230 | 401 | 402 | 401 | 120 mm² |  | 2 | 1 | 1 | 1 | [38 empty] | Total Load R: 2; Total Load Y: 1; Total Load B: 1; Total Load N: 1 | 2 | 1 | 1.3891 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 58 | Pole (PMT) |  | 100 | 17/05/2026, 08:48 | 1 | 228 | 230 | 228 | 401 | 402 | 401 | 120 mm² |  | 2 | 1 | 1 | 0 | [38 empty] | Total Load R: 2; Total Load Y: 1; Total Load B: 1; Total Load N: 0 | 2 | 1 | 1.3891 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 48 | Pole (PMT) |  | 100 | 17/05/2026, 08:38 | 1 | 230 | 230 | 229 | 401 | 402 | 401 | 120 mm² |  | 1 | 1 | 1 | 0 | [38 empty] | Total Load R: 1; Total Load Y: 1; Total Load B: 1; Total Load N: 0 | 1 | 1 | 0.69455 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 45 | Pole (PMT) |  | 100 | 17/05/2026, 08:30 | 1 | 229 | 230 | 229 | 401 | 402 | 401 | 120 mm² |  | 6 | 4 | 3 | 2 | [38 empty] | Total Load R: 6; Total Load Y: 4; Total Load B: 3; Total Load N: 2 | 6 | 3 | 4.1673 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 41 | Pole (PMT) |  | 100 | 17/05/2026, 08:22 | 1 | 229 | 231 | 229 | 404 | 403 | 402 | 120 mm² |  | 2 | 2 | 1 | 0 | [38 empty] | Total Load R: 2; Total Load Y: 2; Total Load B: 1; Total Load N: 0 | 2 | 1 | 1.3995 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 40 | Pole (PMT) |  | 315 | 17/05/2026, 08:16 | 1 | 235 | 236 | 235 | 409 | 406 | 404 | 120 mm² |  | 15 | 41 | 4 | 31 | 120 mm² |  | 8 | 7 | 2 | 5 | [32 empty] | Total Load R: 23; Total Load Y: 48; Total Load B: 6; Total Load N: 36 | 48 | 6 | 10.7948 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 40 | Pole (PMT) | 3 | 315 | 06/06/2026, 21:48 | 2 | 240 | 240 | 239 | 414 | 411 | 411 | 120 mm² |  | 75 | 102 | 50 | 53 | 120 mm² |  | 13 | 36 | 8 | 30 | [32 empty] | Total Load R: 88; Total Load Y: 138; Total Load B: 58; Total Load N: 83 | 138 | 58 | 31.4145 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.953511, 56.657247 | 38 | Pole (PMT) |  | 100 | 17/05/2026, 08:06 | 1 | 235 | 236 | 234 | 408 | 407 | 406 | 120 mm² |  | 2 | 1 | 1 | 0 |  |  | 114 | 115 | 112 | 5 | [32 empty] | Total Load R: 116; Total Load Y: 116; Total Load B: 113; Total Load N: 5 | 116 | 113 | 81.9745 | Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.953511, 56.657247 | 38 | Pole (PMT) | 3 | 100 | 11/06/2026, 07:42 | 2 | 242 | 243 | 241 | 420 | 418 | 417 | 120 mm² |  | 2 | 1 | 1 | 0 | 120 mm² |  | 105 | 101 | 39 | 5 | [32 empty] | Total Load R: 107; Total Load Y: 102; Total Load B: 40; Total Load N: 5 | 107 | 40 | 77.8384 | Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.952749, 56.661989 | 39 | Pole (PMT) |  | 315 | 17/05/2026, 08:01 | 1 | 238 | 240 | 238 | 415 | 411 | 415 | 185 mm² |  | 123 | 142 | 135 | 15 | 185 mm² |  | 54 | 56 | 47 | 14 | [32 empty] | Total Load R: 177; Total Load Y: 198; Total Load B: 182; Total Load N: 29 | 198 | 177 | 45.1818 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.952749, 56.661989 | 39 | Pole (PMT) | 3 | 315 | 11/06/2026, 07:37 | 2 | 245 | 245 | 244 | 425 | 423 | 421 | 120 mm² |  | 158 | 178 | 167 | 15 | 120 mm² |  | 81 | 74 | 78 | 13 | [32 empty] | Total Load R: 239; Total Load Y: 252; Total Load B: 245; Total Load N: 28 | 252 | 239 | 58.8897 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.948438, 56.671079 | 29 | Pole (PMT) |  | 200 | 17/05/2026, 07:54 | 1 | 239 | 242 | 239 | 417 | 413 | 416 | 120 mm² |  | 86 | 81 | 86 | 8 | [38 empty] | Total Load R: 86; Total Load Y: 81; Total Load B: 86; Total Load N: 8 | 86 | 81 | 31.0574 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.948438, 56.671079 | 29 | Pole (PMT) | 3 | 200 | 11/06/2026, 07:31 | 2 | 246 | 247 | 245 | 427 | 425 | 423 | 120 mm² |  | 109 | 95 | 104 | 18 | [38 empty] | Total Load R: 109; Total Load Y: 95; Total Load B: 104; Total Load N: 18 | 109 | 95 | 40.3074 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.947364, 56.665267 | 28 | Pole (PMT) |  | 100 | 17/05/2026, 07:48 | 1 | 236 | 238 | 236 | 409 | 406 | 409 | 120 mm² |  | 100 | 99 | 95 | 5 | [38 empty] | Total Load R: 100; Total Load Y: 99; Total Load B: 95; Total Load N: 5 | 100 | 95 | 70.8409 | Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.947364, 56.665267 | 28 | Pole (PMT) | 5 | 100 | 11/06/2026, 07:26 | 2 | 242 | 244 | 242 | 421 | 420 | 419 | 120 mm² |  | 108 | 99 | 96 | 12 | [38 empty] | Total Load R: 108; Total Load Y: 99; Total Load B: 96; Total Load N: 12 | 108 | 96 | 78.7529 | Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.945698, 56.661696 | 37 | Pole (PMT) |  | 100 | 17/05/2026, 07:44 | 1 | 232 | 234 | 232 | 403 | 403 | 404 | 120 mm² |  | 2 | 1 | 3 | 2 | [38 empty] | Total Load R: 2; Total Load Y: 1; Total Load B: 3; Total Load N: 2 | 3 | 1 | 2.094 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 | 22.945698, 56.661696 | 37 | Pole (PMT) | 3 | 100 | 11/06/2026, 07:20 | 2 | 238 | 239 | 237 | 414 | 412 | 411 | 120 mm² |  | 1 | 0 | 0 | 0 | [38 empty] | Total Load R: 1; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 1 | 0 | 0.71707 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.727904, 56.694638 | 13 | Pole (PMT) |  | 100 | 15/05/2026, 18:06 | 1 | 241 | 244 | 242 | 424 | 421 | 422 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.723291, 56.69725 | 15 | Pole (PMT) |  | 100 | 15/05/2026, 17:55 | 1 | 241 | 240 | 242 | 420 | 419 | 420 | 120 mm² |  | 0 | 1 | 1 | 1 | [38 empty] | Total Load R: 0; Total Load Y: 1; Total Load B: 1; Total Load N: 1 | 1 | 0 | 0.72746 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 14 | Pole (PMT) |  | 100 | 15/05/2026, 17:51 | 1 | 240 | 241 | 240 | 418 | 414 | 419 | 120 mm² |  | 14 | 13 | 13 | 0 | [38 empty] | Total Load R: 14; Total Load Y: 13; Total Load B: 13; Total Load N: 0 | 14 | 13 | 10.136 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 62 | Pole (PMT) |  | 100 | 15/05/2026, 17:45 | 1 | 242 | 240 | 241 | 420 | 419 | 419 | 70 mm² |  | 3 | 4 | 0 | 3 | [38 empty] | Total Load R: 3; Total Load Y: 4; Total Load B: 0; Total Load N: 3 | 4 | 0 | 2.9098 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.737558, 56.60958 | 29 | Ground (GMT) |  | 500 | 14/05/2026, 17:19 | 1 | 242 | 242 | 241 | 419 | 417 | 417 | 185 mm² |  | 10 | 1 | 1 | 4 | 185 mm² |  | 114 | 127 | 147 | 39 | [32 empty] | Total Load R: 124; Total Load Y: 128; Total Load B: 148; Total Load N: 43 | 148 | 124 | 21.4816 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.736839, 56.607726 | 27 | Pole (PMT) |  | 100 | 14/05/2026, 17:08 | 1 | 237 | 236 | 235 | 410 | 409 | 409 | 120 mm² |  | 1 | 1 | 1 | 0 | [38 empty] | Total Load R: 1; Total Load Y: 1; Total Load B: 1; Total Load N: 0 | 1 | 1 | 0.71014 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.758207, 56.581522 | 26 | Pole (PMT) |  | 100 | 14/05/2026, 17:01 | 1 | 241 | 240 | 239 | 417 | 415 | 414 | 120 mm² |  | 2 | 1 | 0 | 0 | [38 empty] | Total Load R: 2; Total Load Y: 1; Total Load B: 0; Total Load N: 0 | 2 | 0 | 1.4445 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.763676, 56.571698 | 6 | Ground (GMT) |  | 500 | 14/05/2026, 16:54 | 1 | 232 | 232 | 231 | 402 | 401 | 402 | 240 mm² |  | 116 | 124 | 122 | 15 | [38 empty] | Total Load R: 116; Total Load Y: 124; Total Load B: 122; Total Load N: 15 | 124 | 116 | 17.2679 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.736196, 56.697051 | 16 | Pole (PMT) |  | 315 | 14/05/2026, 16:43 | 1 | 247 | 247 | 246 | 430 | 427 | 430 | 120 mm² |  | 16 | 12 | 46 | 34 | 120 mm² |  | 0 | 15 | 0 | 17 | [32 empty] | Total Load R: 16; Total Load Y: 27; Total Load B: 46; Total Load N: 51 | 46 | 16 | 10.8762 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.740827, 56.580814 | 7 | Pole (PMT) |  | 100 | 14/05/2026, 16:43 | 1 | 236 | 235 | 235 | 410 | 408 | 406 | 120 mm² |  | 57 | 73 | 58 | 9 | 120 mm² |  | 67 | 78 | 92 | 21 | [32 empty] | Total Load R: 124; Total Load Y: 151; Total Load B: 150; Total Load N: 30 | 151 | 124 | 107.2313 | Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.738234, 56.706015 | 19 | Pole (PMT) |  | 100 | 14/05/2026, 16:36 | 1 | 240 | 241 | 242 | 420 | 421 | 420 | 120 mm² |  | 50 | 27 | 37 | 15 | 240 mm² |  | 25 | 36 | 18 | 13 | [32 empty] | Total Load R: 75; Total Load Y: 63; Total Load B: 55; Total Load N: 28 | 75 | 55 | 54.5596 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.724084, 56.547213 | 8 | Pole (PMT) |  | 100 | 14/05/2026, 16:31 | 1 | 239 | 238 | 237 | 413 | 412 | 410 | 120 mm² |  | 2 | 10 | 2 | 9 | [38 empty] | Total Load R: 2; Total Load Y: 10; Total Load B: 2; Total Load N: 9 | 10 | 2 | 7.1534 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.728851, 56.704217 | 18 | Pole (PMT) |  | 100 | 14/05/2026, 16:31 | 1 | 233 | 234 | 233 | 407 | 403 | 406 | 120 mm² |  | 79 | 85 | 95 | 16 | [38 empty] | Total Load R: 79; Total Load Y: 85; Total Load B: 95; Total Load N: 16 | 95 | 79 | 66.9697 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.708741, 56.54546 | 30 | Pole (PMT) |  | 100 | 14/05/2026, 16:25 | 1 | 238 | 238 | 237 | 413 | 410 | 409 | 120 mm² |  | 1 | 1 | 1 | 1 | [46 empty] | 1 | 1 | 0.71534 | OK - No Upgrade | OK - Balanced | bar: Total Load R to Total Load N
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.725915, 56.719243 | 20 | Pole (PMT) |  | 100 | 14/05/2026, 16:23 | 1 | 237 | 238 | 239 | 412 | 415 | 414 | 120 mm² |  | 17 | 16 | 18 | 5 | [38 empty] | Total Load R: 17; Total Load Y: 16; Total Load B: 18; Total Load N: 5 | 18 | 16 | 12.8449 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.709172, 56.538668 | 9 | Pole (PMT) |  | 100 | 14/05/2026, 16:20 | 1 | 238 | 237 | 236 | 411 | 410 | 409 | 120 mm² |  | 10 | 4 | 3 | 10 | [38 empty] | Total Load R: 10; Total Load Y: 4; Total Load B: 3; Total Load N: 10 | 10 | 3 | 7.1187 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.723724, 56.724659 | 21 | Pole (PMT) |  | 100 | 14/05/2026, 16:18 | 1 | 241 | 244 | 243 | 422 | 418 | 423 | 120 mm² |  | 20 | 18 | 18 | 7 | [38 empty] | Total Load R: 20; Total Load Y: 18; Total Load B: 18; Total Load N: 7 | 20 | 18 | 14.6185 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.697805, 56.541227 | 10 | Pole (PMT) |  | 100 | 14/05/2026, 16:15 | 1 | 233 | 232 | 234 | 404 | 401 | 401 | 120 mm² |  | 54 | 48 | 21 | 16 | [38 empty] | Total Load R: 54; Total Load Y: 48; Total Load B: 21; Total Load N: 16 | 54 | 21 | 37.7864 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.72515, 56.726098 | 22 | Pole (PMT) |  | 100 | 14/05/2026, 16:13 | 1 | 235 | 237 | 236 | 410 | 409 | 413 | 120 mm² |  | 27 | 13 | 10 | 12 | [38 empty] | Total Load R: 27; Total Load Y: 13; Total Load B: 10; Total Load N: 12 | 27 | 10 | 19.1738 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.725179, 56.726058 | 23 | Pole (PMT) |  | 100 | 14/05/2026, 16:12 | 1 | 232 | 234 | 233 | 405 | 403 | 407 | 120 mm² |  | 35 | 32 | 25 | 13 | [38 empty] | Total Load R: 35; Total Load Y: 32; Total Load B: 25; Total Load N: 13 | 35 | 25 | 24.5518 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.72516, 56.726136 | 24 | Pole (PMT) |  | 100 | 14/05/2026, 16:11 | 1 | 233 | 236 | 234 | 408 | 409 | 405 | 120 mm² |  | 0 | 1 | 0 | 1 | [38 empty] | Total Load R: 0; Total Load Y: 1; Total Load B: 0; Total Load N: 1 | 1 | 0 | 0.70668 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.725093, 56.726182 | 25 | Pole (PMT) |  | 100 | 14/05/2026, 16:09 | 1 | 232 | 236 | 233 | 407 | 407 | 405 | 120 mm² |  | 25 | 6 | 1 | 15 | [38 empty] | Total Load R: 25; Total Load Y: 6; Total Load B: 1; Total Load N: 15 | 25 | 1 | 17.6236 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.695279, 56.536166 | 12 | Pole (PMT) |  | 100 | 14/05/2026, 16:10 | 1 | 234 | 233 | 232 | 405 | 406 | 402 | 120 mm² |  | 56 | 57 | 45 | 10 | [38 empty] | Total Load R: 56; Total Load Y: 57; Total Load B: 45; Total Load N: 10 | 57 | 45 | 39.9844 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.725201, 56.726081 | 34 | Pole (PMT) |  | 200 | 14/05/2026, 16:08 | 1 | 238 | 241 | 237 | 417 | 410 | 416 | 240 mm² |  | 22 | 40 | 65 | 35 | [38 empty] | Total Load R: 22; Total Load Y: 40; Total Load B: 65; Total Load N: 35 | 65 | 22 | 23.4736 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.725214, 56.726139 | 26 | Pole (PMT) |  | 100 | 14/05/2026, 16:06 | 1 | 229 | 230 | 229 | 400 | 400 | 400 | 120 mm² |  | 20 | 31 | 19 | 10 | [38 empty] | Total Load R: 20; Total Load Y: 31; Total Load B: 19; Total Load N: 10 | 31 | 19 | 21.4774 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.690227, 56.533144 | 13 | Pole (PMT) |  | 200 | 14/05/2026, 16:03 | 1 | 236 | 235 | 234 | 404 | 405 | 404 | 120 mm² |  | 41 | 34 | 62 | 21 | 120 mm² |  | 7 | 41 | 7 | 34 | [32 empty] | Total Load R: 48; Total Load Y: 75; Total Load B: 69; Total Load N: 55 | 75 | 48 | 26.2406 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.696, 56.518856 | 14 | Pole (PMT) |  | 100 | 14/05/2026, 15:53 | 1 | 238 | 230 | 228 | 413 | 410 | 401 | 120 mm² |  | 2 | 1 | 0 | 0 | [38 empty] | Total Load R: 2; Total Load Y: 1; Total Load B: 0; Total Load N: 0 | 2 | 0 | 1.4307 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.684034, 56.524462 | 15 | Pole (PMT) |  | 100 | 14/05/2026, 15:45 | 1 | 231 | 230 | 229 | 404 | 405 | 404 | 120 mm² |  | 12 | 14 | 14 | 5 | [38 empty] | Total Load R: 12; Total Load Y: 14; Total Load B: 14; Total Load N: 5 | 14 | 12 | 9.7965 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.623134, 56.472349 | 22 | Pole (PMT) |  | 100 | 14/05/2026, 15:30 | 1 | 218 | 229 | 219 | 412 | 411 | 416 | 120 mm² |  | 1 | 1 | 0 | 0 | [38 empty] | Total Load R: 1; Total Load Y: 1; Total Load B: 0; Total Load N: 0 | 1 | 0 | 0.7136 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.618027, 56.466853 | 24 | Pole (PMT) |  | 100 | 14/05/2026, 15:24 | 1 | 238 | 240 | 238 | 413 | 412 | 414 | 120 mm² |  | 10 | 4 | 1 | 8 | [38 empty] | Total Load R: 10; Total Load Y: 4; Total Load B: 1; Total Load N: 8 | 10 | 1 | 7.1534 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.619467, 56.474076 | 23 | Pole (PMT) |  | 100 | 14/05/2026, 15:18 | 1 | 237 | 228 | 234 | 387 | 412 | 413 | 120 mm² |  | 16 | 2 | 10 | 11 | [38 empty] | Total Load R: 16; Total Load Y: 2; Total Load B: 10; Total Load N: 11 | 16 | 2 | 10.7249 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.676783, 56.846917 | 28 | Pole (PMT) |  | 100 | 14/05/2026, 15:14 | 1 | 233 | 234 | 232 | 409 | 405 | 407 | 240 mm² |  | 35 | 60 | 47 | 20 | [38 empty] | Total Load R: 35; Total Load Y: 60; Total Load B: 47; Total Load N: 20 | 60 | 35 | 42.5045 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.627375, 56.476717 | 21 | Pole (PMT) |  | 100 | 14/05/2026, 15:12 | 1 | 240 | 241 | 237 | 416 | 141 | 405 | 120 mm² |  | 1 | 1 | 12 | 10 | [38 empty] | Total Load R: 1; Total Load Y: 1; Total Load B: 12; Total Load N: 10 | 12 | 1 | 8.6464 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.672818, 56.844668 | 27 | Pole (PMT) |  | 100 | 14/05/2026, 15:08 | 1 | 230 | 230 | 229 | 400 | 400 | 400 | 120 mm² |  | 0 | 0 | 0 | 0 | 70 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.636601, 56.486417 | 20 | Pole (PMT) |  | 100 | 14/05/2026, 15:06 | 1 | 240 | 241 | 240 | 416 | 414 | 410 | 120 mm² |  | 11 | 12 | 4 | 10 | [38 empty] | Total Load R: 11; Total Load Y: 12; Total Load B: 4; Total Load N: 10 | 12 | 4 | 8.6464 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.667212, 56.84377 | 29 | Pole (PMT) |  | 200 | 14/05/2026, 14:59 | 1 | 234 | 238 | 234 | 411 | 412 | 408 | 240 mm² |  | 37 | 50 | 60 | 22 | 120 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 37; Total Load Y: 50; Total Load B: 60; Total Load N: 22 | 60 | 37 | 21.3562 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.649298, 56.49394 | 19 | Pole (PMT) |  | 100 | 14/05/2026, 14:58 | 1 | 241 | 242 | 240 | 418 | 416 | 415 | 120 mm² |  | 2 | 1 | 1 | 0 | [38 empty] | Total Load R: 2; Total Load Y: 1; Total Load B: 1; Total Load N: 0 | 2 | 1 | 1.448 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.661678, 56.842138 | 30 | Pole (PMT) |  | 100 | 14/05/2026, 14:53 | 1 | 235 | 235 | 236 | 411 | 405 | 407 | 240 mm² |  | 3 | 66 | 61 | 65 | [38 empty] | Total Load R: 3; Total Load Y: 66; Total Load B: 61; Total Load N: 65 | 66 | 3 | 46.9836 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.649664, 56.494239 | 18 | Pole (PMT) |  | 100 | 14/05/2026, 14:56 | 1 | 240 | 241 | 239 | 417 | 413 | 417 | 120 mm² |  | 2 | 1 | 1 | 0 | [38 empty] | Total Load R: 2; Total Load Y: 1; Total Load B: 1; Total Load N: 0 | 2 | 1 | 1.4445 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.656411, 56.843959 | 31 | Ground (GMT) |  | 500 | 14/05/2026, 14:48 | 1 | 230 | 232 | 230 | 400 | 400 | 402 | 185 mm² |  | 176 | 88 | 68 | 83 | [38 empty] | Total Load R: 176; Total Load Y: 88; Total Load B: 68; Total Load N: 83 | 176 | 68 | 24.3873 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.653022, 56.843721 | 32 | Pole (PMT) |  | 100 | 14/05/2026, 14:50 | 1 | 230 | 234 | 230 | 404 | 400 | 403 | 120 mm² |  | 6 | 0 | 0 | 5 | [38 empty] | Total Load R: 6; Total Load Y: 0; Total Load B: 0; Total Load N: 5 | 6 | 0 | 4.1985 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 | 22.656467, 56.843836 | 33 | Pole (PMT) |  | 100 | 14/05/2026, 14:48 | 1 | 230 | 234 | 230 | 405 | 400 | 402 | 120 mm² |  | 31 | 0 | 27 | 50 | [38 empty] | Total Load R: 31; Total Load Y: 0; Total Load B: 27; Total Load N: 50 | 31 | 0 | 21.7459 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.681597, 56.515693 | 16 | Pole (PMT) |  | 200 | 14/05/2026, 14:36 | 1 | 236 | 237 | 236 | 410 | 407 | 408 | 185 mm² |  | 143 | 150 | 118 | 24 | [38 empty] | Total Load R: 143; Total Load Y: 150; Total Load B: 118; Total Load N: 24 | 150 | 118 | 53.2606 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.683749, 56.513616 | 28 | Pole (PMT) |  | 100 | 14/05/2026, 14:32 | 1 | 240 | 241 | 239 | 417 | 414 | 415 | 185 mm² |  | 16 | 17 | 10 | 5 | 120 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 16; Total Load Y: 17; Total Load B: 10; Total Load N: 5 | 17 | 10 | 12.2785 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.687015, 56.514344 | 25 | Pole (PMT) |  | 100 | 14/05/2026, 14:22 | 1 | 238 | 236 | 239 | 413 | 411 | 408 | 120 mm² |  | 29 | 94 | 15 | 74 | [38 empty] | Total Load R: 29; Total Load Y: 94; Total Load B: 15; Total Load N: 74 | 94 | 15 | 67.2417 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.685053, 56.519267 | 17 | Pole (PMT) |  | 315 | 14/05/2026, 14:16 | 1 | 243 | 245 | 243 | 423 | 419 | 423 | 185 mm² |  | 81 | 53 | 73 | 28 | 120 mm² |  | 73 | 52 | 93 | 28 | [32 empty] | Total Load R: 154; Total Load Y: 105; Total Load B: 166; Total Load N: 56 | 166 | 105 | 38.6099 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 03 | Ground (GMT) |  | 500 | 13/05/2026, 21:25 | 1 | 245 | 246 | 246 | 426 | 424 | 430 | 240 mm² |  | 8 | 0 | 0 | 0 | [38 empty] | Total Load R: 8; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 8 | 0 | 1.1806 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 05 | Pole (PMT) |  | 100 | 13/05/2026, 16:26 | 1 | 245 | 244 | 244 | 424 | 426 | 425 | 120 mm² |  | 10 | 13 | 11 | 5 | [38 empty] | Total Load R: 10; Total Load Y: 13; Total Load B: 11; Total Load N: 5 | 13 | 10 | 9.5471 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 04 | Pole (PMT) |  | 100 | 13/05/2026, 16:21 | 1 | 244 | 246 | 245 | 426 | 427 | 426 | 120 mm² |  | 18 | 0 | 1 | 14 | [38 empty] | Total Load R: 18; Total Load Y: 0; Total Load B: 1; Total Load N: 14 | 18 | 0 | 13.2814 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 56 | Pole (PMT) |  | 100 | 13/05/2026, 16:18 | 1 | 234 | 235 | 233 | 408 | 405 | 406 | 120 mm² |  | 1 | 0 | 25 | 19 | [38 empty] | Total Load R: 1; Total Load Y: 0; Total Load B: 25; Total Load N: 19 | 25 | 0 | 17.6669 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 02 | Pole (PMT) |  | 100 | 13/05/2026, 16:13 | 1 | 245 | 245 | 243 | 428 | 422 | 424 | 120 mm² |  | 4 | 23 | 57 | 19 | 120 mm² |  | 16 | 0 | 10 | 8 | [32 empty] | Total Load R: 20; Total Load Y: 23; Total Load B: 67; Total Load N: 27 | 67 | 20 | 49.6683 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN2 |  | 01 | Pole (PMT) |  | 100 | 13/05/2026, 16:07 | 1 | 247 | 246 | 244 | 430 | 427 | 426 | 240 mm² |  | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 12 | 8 | [32 empty] | Total Load R: 1; Total Load Y: 0; Total Load B: 12; Total Load N: 8 | 12 | 0 | 8.9374 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 01 | Ground (GMT) |  | 500 | 13/05/2026, 16:02 | 1 | 234 | 235 | 235 | 406 | 405 | 407 | 120 mm² |  | 93 | 35 | 29 | 55 | [38 empty] | Total Load R: 93; Total Load Y: 35; Total Load B: 29; Total Load N: 55 | 93 | 29 | 13.0798 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 02 | Ground (GMT) |  | 500 | 13/05/2026, 15:54 | 1 | 245 | 246 | 246 | 426 | 426 | 428 | 185 mm² |  | 101 | 62 | 33 | 54 | [38 empty] | Total Load R: 101; Total Load Y: 62; Total Load B: 33; Total Load N: 54 | 101 | 33 | 14.9046 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 09 | Pole (PMT) |  | 100 | 13/05/2026, 15:48 | 1 | 230 | 231 | 230 | 400 | 400 | 400 | 120 mm² |  | 7 | 6 | 5 | 1 | [38 empty] | Total Load R: 7; Total Load Y: 6; Total Load B: 5; Total Load N: 1 | 7 | 5 | 4.8497 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 05 | Ground (GMT) |  | 1000 | 13/05/2026, 15:43 | 1 | 246 | 246 | 245 | 428 | 427 | 428 | 240 mm² |  | 50 | 48 | 49 | 0 | [38 empty] | Total Load R: 50; Total Load Y: 48; Total Load B: 49; Total Load N: 0 | 50 | 48 | 3.7066 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 06 | Pole (PMT) |  | 100 | 13/05/2026, 15:37 | 1 | 244 | 242 | 240 | 423 | 420 | 419 | 185 mm² |  | 25 | 48 | 65 | 32 | [38 empty] | Total Load R: 25; Total Load Y: 48; Total Load B: 65; Total Load N: 32 | 65 | 25 | 47.6227 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 8 | Pole (PMT) |  | 100 | 13/05/2026, 15:26 | 1 | 238 | 239 | 238 | 414 | 415 | 414 | 120 mm² |  | 30 | 14 | 8 | 18 | [38 empty] | Total Load R: 30; Total Load Y: 14; Total Load B: 8; Total Load N: 18 | 30 | 8 | 21.5121 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 07 | Pole (PMT) |  | 100 | 13/05/2026, 15:21 | 1 | 240 | 239 | 238 | 417 | 414 | 413 | 185 mm² |  | 7 | 26 | 3 | 15 | [38 empty] | Total Load R: 7; Total Load Y: 26; Total Load B: 3; Total Load N: 15 | 26 | 3 | 18.7789 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 4 | Ground (GMT) |  | 500 | 13/05/2026, 15:16 | 1 | 243 | 244 | 242 | 422 | 420 | 421 | 185 mm² |  | 320 | 290 | 318 | 135 | [38 empty] | Total Load R: 320; Total Load Y: 290; Total Load B: 318; Total Load N: 135 | 320 | 290 | 46.7792 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 3 | Ground (GMT) |  | 1000 | 13/05/2026, 15:09 | 1 | 238 | 239 | 238 | 415 | 416 | 414 | 185 mm² |  | 365 | 330 | 290 | 171 | [38 empty] | Total Load R: 365; Total Load Y: 330; Total Load B: 290; Total Load N: 171 | 365 | 290 | 26.2362 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 10 | Pole (PMT) |  | 200 | 13/05/2026, 14:51 | 1 | 251 | 250 | 250 | 435 | 436 | 433 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 11 | Pole (PMT) |  | 100 | 13/05/2026, 14:45 | 1 | 244 | 243 | 244 | 423 | 423 | 420 | 120 mm² |  | 18 | 35 | 1 | 20 | [38 empty] | Total Load R: 18; Total Load Y: 35; Total Load B: 1; Total Load N: 20 | 35 | 1 | 25.643 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 12 | Pole (PMT) |  | 315 | 13/05/2026, 14:38 | 1 | 243 | 243 | 242 | 423 | 421 | 423 | 185 mm² |  | 42 | 36 | 60 | 21 |  |  | 0 | 18 | 29 | 29 | 120 mm² |  | 41 | 17 | 25 | 21 | [26 empty] | Total Load R: 83; Total Load Y: 71; Total Load B: 114; Total Load N: 71 | 114 | 71 | 26.5152 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN3 |  | 61 | Pole (PMT) |  | 100 | 13/05/2026, 14:29 | 1 | 245 | 246 | 245 | 426 | 425 | 426 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hamra AlDaroo | Hamra AlDaroo | K_LN1 |  | 3 | Pole (PMT) |  | 200 | 13/05/2026, 14:22 | 1 | 246 | 245 | 246 | 427 | 429 | 426 | 120 mm² |  | 50 | 42 | 37 | 15 |  |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 50; Total Load Y: 42; Total Load B: 37; Total Load N: 15 | 50 | 37 | 18.4896 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 |  | 02 | Pole (PMT) |  | 200 | 13/05/2026, 14:12 | 1 | 245 | 246 | 247 | 428 | 430 | 429 |  |  | 15 | 30 | 17 | 12 | [38 empty] | Total Load R: 15; Total Load Y: 30; Total Load B: 17; Total Load N: 12 | 30 | 15 | 11.1198 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.724789, 56.620395 | 01 | Pole (PMT) |  | 200 | 13/05/2026, 14:04 | 1 | 242 | 245 | 245 | 424 | 425 | 426 | 120 mm² |  | 5 | 6 | 5 | 0 |  |  | 70 | 23 | 22 | 50 | [32 empty] | Total Load R: 75; Total Load Y: 29; Total Load B: 27; Total Load N: 50 | 75 | 27 | 27.5396 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Hamra AlDaroo | K_LN1 | 22.724922, 56.620669 | 04 | Pole (PMT) |  | 315 | 12/05/2026, 13:54 | 1 | 246 | 247 | 246 | 430 | 427 | 428 | 120 mm² |  | 48 | 25 | 24 | 18 | [38 empty] | Total Load R: 48; Total Load Y: 25; Total Load B: 24; Total Load N: 18 | 48 | 24 | 11.3491 | OK - No Upgrade | Need to Balance

## Masrooq
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Masrooq | Masrooq | K_LN2 | 22.784807, 55.996691 | 6 | Pole (PMT) |  | 315 | 20/05/2026, 12:08 | 1 | 245 | 245 | 245 | 431 | 420 | 420 | 185 mm² |  | 132 | 141 | 101 | 14 | [38 empty] | Total Load R: 132; Total Load Y: 141; Total Load B: 101; Total Load N: 14 | 141 | 101 | 33.4154 | OK - No Upgrade | Need to Balance
Masrooq | Masrooq | K_LN2 | 22.789156, 56.003392 | 5 | Pole (PMT) |  | 315 | 20/05/2026, 12:16 | 1 | 243 | 244 | 244 | 416 | 417 | 418 | 185 mm² |  | 137 | 122 | 130 | 23 | [38 empty] | Total Load R: 137; Total Load Y: 122; Total Load B: 130; Total Load N: 23 | 137 | 122 | 31.3375 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN2 | 22.77422, 55.9931 | 4 | Pole (PMT) |  | 100 | 20/05/2026, 12:03 | 1 | 245 | 242 | 244 | 418 | 417 | 420 | 120 mm² |  | 15 | 41 | 172 | 7 | [38 empty] | Total Load R: 15; Total Load Y: 41; Total Load B: 172; Total Load N: 7 | 172 | 15 | 124.5275 | Upgrade | Need to Balance
Masrooq | Masrooq | K_LN2 | 22.783506, 55.994187 | 3 | Pole (PMT) |  | 315 | 20/05/2026, 12:13 | 1 | 247 | 246 | 247 | 424 | 424 | 424 | 120 mm² |  | 154 | 269 | 250 | 98 | 120 mm² |  | 137 | 82 | 87 | 21 | [32 empty] | Total Load R: 291; Total Load Y: 351; Total Load B: 337; Total Load N: 119 | 351 | 291 | 81.832 | Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN2 | 22.787198, 56.000406 | 2 | Pole (PMT) |  | 315 | 20/05/2026, 12:12 | 1 | 252 | 254 | 253 | 432 | 433 | 434 | 185 mm² |  | 300 | 200 | 258 | 66 | 185 mm² |  | 63 | 65 | 55 | 14 | [32 empty] | Total Load R: 363; Total Load Y: 265; Total Load B: 313; Total Load N: 80 | 363 | 265 | 86.2264 | Upgrade | Need to Balance
Masrooq | Masrooq | K_LN2 | 22.794371, 56.00735 | 1 | Ground (GMT) |  | 500 | 20/05/2026, 12:25 | 1 | 244 | 245 | 245 | 416 | 417 | 419 | 185 mm² |  | 127 | 83 | 57 | 58 | 185 mm² |  | 96 | 116 | 98 | 40 | 185 mm² |  | 108 | 60 | 65 | 23 | [26 empty] | Total Load R: 331; Total Load Y: 259; Total Load B: 220; Total Load N: 121 | 331 | 220 | 47.6993 | OK - No Upgrade | Need to Balance
Masrooq | Masrooq | K_LN1 | 22.853302, 56.023898 | 16 | Ground (GMT) |  | 500 | 20/05/2026, 12:51 | 1 | 241 | 240 | 241 | 412 | 413 | 414 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.801492, 56.019843 | 15 | Ground (GMT) |  | 500 | 20/05/2026, 12:31 | 1 | 246 | 246 | 245 | 420 | 420 | 421 | 240 mm² |  | 45 | 40 | 30 | 22 | [38 empty] | Total Load R: 45; Total Load Y: 40; Total Load B: 30; Total Load N: 22 | 45 | 30 | 6.5472 | OK - No Upgrade | Need to Balance
Masrooq | Masrooq | K_LN1 | 22.855746, 56.024164 | 14 | Ground (GMT) |  | 1000 | 20/05/2026, 12:57 | 1 | 238 | 237 | 238 | 402 | 402 | 403 |  |  | 720 | 931 | 752 | 100 | [38 empty] | Total Load R: 720; Total Load Y: 931; Total Load B: 752; Total Load N: 100 | 931 | 720 | 64.8241 | OK - No Upgrade | Need to Balance
Masrooq | Masrooq | K_LN1 | 22.847281, 56.023834 | 13 | Pole (PMT) |  | 315 | 20/05/2026, 12:44 | 1 | 239 | 240 | 242 | 412 | 414 | 414 | 185 mm² |  | 88 | 66 | 54 | 23 |  |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 88; Total Load Y: 66; Total Load B: 54; Total Load N: 23 | 88 | 54 | 19.9356 | OK - No Upgrade | Need to Balance
Masrooq | Masrooq | K_LN1 | 22.859674, 56.029307 | 12 | Pole (PMT) |  | 315 | 20/05/2026, 13:39 | 1 | 237 | 238 | 238 | 406 | 403 | 407 | 120 mm² |  | 151 | 236 | 142 | 35 | 120 mm² |  | 15 | 10 | 11 | 4 | [32 empty] | Total Load R: 166; Total Load Y: 246; Total Load B: 153; Total Load N: 39 | 246 | 153 | 54.9176 | OK - No Upgrade | Need to Balance
Masrooq | Masrooq | K_LN1 | 22.865642, 56.031987 | 112 | Ground (GMT) |  | 1000 | 20/05/2026, 13:21 | 1 | 239 | 240 | 240 | 410 | 411 | 410 | 240 mm² |  | 232 | 183 | 198 | 49 | 240 mm² |  | 52 | 93 | 93 | 30 | [32 empty] | Total Load R: 284; Total Load Y: 276; Total Load B: 291; Total Load N: 79 | 291 | 276 | 20.6651 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.865765, 56.031986 | 111 | Ground (GMT) |  | 1000 | 20/05/2026, 13:19 | 1 | 238 | 239 | 239 | 407 | 409 | 406 | 240 mm² |  | 276 | 271 | 242 | 42 | 240 mm² |  | 304 | 308 | 325 | 33 | [32 empty] | Total Load R: 580; Total Load Y: 579; Total Load B: 567; Total Load N: 75 | 580 | 567 | 40.8868 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.882656, 56.069821 | 2 | Ground (GMT) |  | 500 | 18/05/2026, 12:41 | 1 | 239 | 240 | 240 | 409 | 411 | 410 | 300 mm² |  | 127 | 110 | 116 | 13 | [38 empty] | Total Load R: 127; Total Load Y: 110; Total Load B: 116; Total Load N: 13 | 127 | 110 | 17.9936 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.861867, 56.095349 | 9 | Pole (PMT) |  | 100 | 28/05/2026, 13:35 | 1 | 238 | 239 | 239 | 408 | 408 | 408 | 120 mm² |  | 52 | 57 | 56 | 2 | [38 empty] | Total Load R: 52; Total Load Y: 57; Total Load B: 56; Total Load N: 2 | 57 | 52 | 40.2806 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.861867, 56.095349 | 9 | Pole (PMT) |  | 100 | 08/06/2026, 10:27 | 2 | 237 | 236 | 236 | 216 | 215 | 214 | 120 mm² |  | 52 | 51 | 52 | 4 | [38 empty] | Total Load R: 52; Total Load Y: 51; Total Load B: 52; Total Load N: 4 | 52 | 51 | 19.4544 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.859014, 56.092206 | 8 | Pole (PMT) |  | 100 | 18/05/2026, 12:15 | 1 | 232 | 233 | 233 | 398 | 399 | 398 | 120 mm² |  | 87 | 89 | 81 | 4 | [38 empty] | Total Load R: 87; Total Load Y: 89; Total Load B: 81; Total Load N: 4 | 89 | 81 | 61.3527 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.859014, 56.092206 | 8 | Pole (PMT) |  | 100 | 08/06/2026, 10:23 | 2 | 234 | 232 | 233 | 401 | 413 | 400 | 120 mm² |  | 89 | 90 | 90 | 3 | [38 empty] | Total Load R: 89; Total Load Y: 90; Total Load B: 90; Total Load N: 3 | 90 | 89 | 62.5097 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.853201, 56.088693 | 7 | Pole (PMT) |  | 200 | 18/05/2026, 12:17 | 1 | 238 | 238 | 239 | 408 | 409 | 408 | 120 mm² |  | 32 | 30 | 31 | 3 | [38 empty] | Total Load R: 32; Total Load Y: 30; Total Load B: 31; Total Load N: 3 | 32 | 30 | 11.3068 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.853201, 56.088693 | 7 | Pole (PMT) |  | 200 | 08/06/2026, 10:19 | 2 | 238 | 237 | 240 | 405 | 415 | 403 | 120 mm² |  | 33 | 34 | 34 | 2 | [38 empty] | Total Load R: 33; Total Load Y: 34; Total Load B: 34; Total Load N: 2 | 34 | 33 | 11.9252 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.850006, 56.081099 | 6 | Pole (PMT) |  | 100 | 28/05/2026, 13:34 | 1 | 235 | 235 | 236 | 403 | 404 | 403 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.850006, 56.081099 | 6 | Pole (PMT) |  | 100 | 08/06/2026, 10:15 | 2 | 235 | 236 | 235 | 403 | 404 | 403 | 120 mm² |  | 56 | 57 | 57 | 2 | [38 empty] | Total Load R: 56; Total Load Y: 57; Total Load B: 57; Total Load N: 2 | 57 | 56 | 39.7869 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.853109, 56.084358 | 5 | Pole (PMT) |  | 100 | 18/05/2026, 12:21 | 1 | 240 | 239 | 239 | 414 | 413 | 414 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.855922, 56.082551 | 4 | Pole (PMT) |  | 100 | 18/05/2026, 12:21 | 1 | 234 | 236 | 234 | 403 | 404 | 403 | 120 mm² |  | 77 | 83 | 83 | 2 | [38 empty] | Total Load R: 77; Total Load Y: 83; Total Load B: 83; Total Load N: 2 | 83 | 77 | 57.9354 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.855922, 56.082551 | 4 | Pole (PMT) |  | 100 | 08/06/2026, 10:05 | 2 | 233 | 234 | 234 | 402 | 401 | 401 | 120 mm² |  | 82 | 82 | 83 | 2 | [38 empty] | Total Load R: 82; Total Load Y: 82; Total Load B: 83; Total Load N: 2 | 83 | 82 | 57.7916 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.856392, 56.083074 | 3 | Pole (PMT) |  | 315 | 18/05/2026, 12:21 | 1 | 240 | 240 | 239 | 414 | 412 | 412 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 22.856392, 56.083074 | 3 | Pole (PMT) |  | 315 |  | 2 | 240 | 240 | 239 | 411 | 412 | 411 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Masrooq | Masrooq | K_LN1 | 23.580032, 56.57179 | 10 | Pole (PMT) |  | 315 | 20/05/2026, 13:04 | 1 | 239 | 240 | 240 | 407 | 408 | 408 | 120 mm² |  | 163 | 67 | 81 | 74 | [38 empty] | Total Load R: 163; Total Load Y: 67; Total Load B: 81; Total Load N: 74 | 163 | 67 | 36.4781 | OK - No Upgrade | Need to Balance
Masrooq | Masrooq | K_LN1 | 23.273949, 56.385169 | 1 | Ground (GMT) |  | 500 | 18/05/2026, 12:50 | 1 | 239 | 240 | 241 | 410 | 413 | 412 | 300 mm² |  | 82 | 29 | 54 | 44 | [38 empty] | Total Load R: 82; Total Load Y: 29; Total Load B: 54; Total Load N: 44 | 82 | 29 | 11.6463 | OK - No Upgrade | Need to Balance

## Al Rob’a AlKhali
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Masrooq | Al Rob’a AlKhali | K_LN1 | 22.247998, 55.562671 | 4 | Pole (PMT) |  | 100 | 19/05/2026, 13:00 | 1 | 249 | 248 | 249 | 429 | 428 | 429 |  |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Masrooq | Al Rob’a AlKhali | K_LN1 | 22.247998, 55.562671 | 4 | Pole (PMT) |  | 100 | 11/06/2026, 11:55 | 2 | 245 | 245 | 244 | 422 | 433 | 423 | 185 mm² |  | 95 | 83 | 70 | 20 | [38 empty] | Total Load R: 95; Total Load Y: 83; Total Load B: 70; Total Load N: 20 | 95 | 70 | 69.4379 | OK - No Upgrade | Need to Balance
Masrooq | Al Rob’a AlKhali | K_LN1 | 22.248976, 55.560888 | 3 | Pole (PMT) |  | 200 | 19/05/2026, 13:04 | 1 | 247 | 248 | 246 | 428 | 426 | 428 | 120 mm² |  | 65 | 57 | 64 | 15 | [38 empty] | Total Load R: 65; Total Load Y: 57; Total Load B: 64; Total Load N: 15 | 65 | 57 | 24.0928 | OK - No Upgrade | OK - Balanced
Masrooq | Al Rob’a AlKhali | K_LN1 | 22.247998, 55.562671 | 2 | Pole (PMT) |  | 315 | 19/05/2026, 12:22 | 1 | 255 | 255 | 254 | 441 | 441 | 441 | 120 mm² |  | 14 | 11 | 12 | 4 | [38 empty] | Total Load R: 14; Total Load Y: 11; Total Load B: 12; Total Load N: 4 | 14 | 11 | 3.3948 | OK - No Upgrade | Need to Balance
Masrooq | Al Rob’a AlKhali | K_LN1 | 22.247998, 55.562671 | 2 | Pole (PMT) |  | 315 | 11/06/2026, 11:35 | 2 | 251 | 250 | 249 | 434 | 431 | 429 | 120 mm² |  | 16 | 11 | 16 | 5 | [38 empty] | Total Load R: 16; Total Load Y: 11; Total Load B: 16; Total Load N: 5 | 16 | 11 | 3.8182 | OK - No Upgrade | Need to Balance
Masrooq | Al Rob’a AlKhali | K_LN4 | 22.237265, 55.546383 | 502 | Ground (GMT) |  | 1000 | 21/05/2026, 12:53 | 1 | 251 | 251 | 252 | 434 | 433 | 432 | 300 mm² |  | 263 | 177 | 142 | 103 | [38 empty] | Total Load R: 263; Total Load Y: 177; Total Load B: 142; Total Load N: 103 | 263 | 142 | 19.77 | OK - No Upgrade | Need to Balance
Masrooq | Al Rob’a AlKhali | K_LN4 | 22.237831, 55.546037 | 403 | Ground (GMT) |  | 500 | 21/05/2026, 12:50 | 1 | 249 | 248 | 247 | 436 | 435 | 434 | 300 mm² |  | 74 | 68 | 80 | 14 | [38 empty] | Total Load R: 74; Total Load Y: 68; Total Load B: 80; Total Load N: 14 | 80 | 68 | 12.0828 | OK - No Upgrade | OK - Balanced
Masrooq | Al Rob’a AlKhali | K_LN4 | 22.238156, 55.546037 | 402 | Ground (GMT) |  | 1000 | 21/05/2026, 12:47 | 1 | 249 | 250 | 248 | 434 | 435 | 434 | 300 mm² |  | 153 | 110 | 111 | 34 | [38 empty] | Total Load R: 153; Total Load Y: 110; Total Load B: 111; Total Load N: 34 | 153 | 110 | 11.5012 | OK - No Upgrade | Need to Balance
Masrooq | Al Rob’a AlKhali | K_LN5 | 22.228414, 55.545632 | 202 | Ground (GMT) |  | 1000 | 18/05/2026, 23:01 | 1 | 248 | 247 | 248 | 437 | 438 | 436 | 300 mm² |  | 179 | 168 | 170 | 30 | [38 empty] | Total Load R: 179; Total Load Y: 168; Total Load B: 170; Total Load N: 30 | 179 | 168 | 13.5486 | OK - No Upgrade | OK - Balanced
Masrooq | Al Rob’a AlKhali | K_LN5 | 22.228443, 55.545646 | 201 | Ground (GMT) |  | 1000 | 18/05/2026, 23:00 | 1 | 247 | 248 | 247 | 438 | 437 | 438 | 300 mm² |  | 367 | 350 | 323 | 28 | [38 empty] | Total Load R: 367; Total Load Y: 350; Total Load B: 323; Total Load N: 28 | 367 | 323 | 27.842 | OK - No Upgrade | OK - Balanced
Masrooq | Al Rob’a AlKhali | K_LN5 | 22.222186, 55.540306 | 7 | Ground (GMT) |  | 1000 | 18/05/2026, 22:43 | 1 | 249 | 248 | 249 | 434 | 435 | 434 | 300 mm² |  | 228 | 226 | 211 | 16 | [38 empty] | Total Load R: 228; Total Load Y: 226; Total Load B: 211; Total Load N: 16 | 228 | 211 | 17.139 | OK - No Upgrade | OK - Balanced
Masrooq | Al Rob’a AlKhali | K_LN5 | 22.215028, 55.530826 | 6 | Ground (GMT) |  | 500 | 18/05/2026, 22:43 | 1 | 250 | 249 | 249 | 435 | 434 | 434 | 300 mm² |  | 6 | 34 | 15 | 25 | [38 empty] | Total Load R: 6; Total Load Y: 34; Total Load B: 15; Total Load N: 25 | 34 | 6 | 5.1234 | OK - No Upgrade | Need to Balance
Masrooq | Al Rob’a AlKhali | K_LN4 | 22.232228, 55.545493 | 302 | Ground (GMT) |  | 1000 | 21/05/2026, 12:36 | 1 | 249 | 248 | 247 | 435 | 434 | 436 | 300 mm² |  | 115 | 133 | 134 | 17 | [38 empty] | Total Load R: 115; Total Load Y: 133; Total Load B: 134; Total Load N: 17 | 134 | 115 | 10.0961 | OK - No Upgrade | OK - Balanced
Masrooq | Al Rob’a AlKhali | K_LN4 | 22.237831, 55.546037 | 301 | Ground (GMT) |  | 1000 | 21/05/2026, 12:36 | 1 | 250 | 249 | 248 | 436 | 435 | 436 | 300 mm² |  | 205 | 212 | 183 | 43 | [38 empty] | Total Load R: 205; Total Load Y: 212; Total Load B: 183; Total Load N: 43 | 212 | 183 | 16.0097 | OK - No Upgrade | OK - Balanced
Masrooq | Al Rob’a AlKhali | K_LN4 | 22.237831, 55.546037 | 401 | Ground (GMT) |  | 1000 | 18/05/2026, 22:33 | 1 | 251 | 250 | 251 | 435 | 436 | 435 | 300 mm² |  | 281 | 232 | 160 | 97 | [38 empty] | Total Load R: 281; Total Load Y: 232; Total Load B: 160; Total Load N: 97 | 281 | 160 | 21.1717 | OK - No Upgrade | Need to Balance
Masrooq | Al Rob’a AlKhali | K_LN4 | 22.236104, 55.546952 | 2 | Ground (GMT) |  | 1000 | 16/05/2026, 11:38 | 1 | 251 | 251 | 252 | 434 | 433 | 431 |  |  | 263 | 177 | 142 | 103 | [38 empty] | Total Load R: 263; Total Load Y: 177; Total Load B: 142; Total Load N: 103 | 263 | 142 | 19.77 | OK - No Upgrade | Need to Balance
Masrooq | Al Rob’a AlKhali | K_LN4 | 22.236082, 55.546944 | 501 | Ground (GMT) |  | 1000 | 18/05/2026, 22:49 | 1 | 253 | 252 | 251 | 438 | 436 | 438 | 300 mm² |  | 169 | 203 | 147 | 55 | [38 empty] | Total Load R: 169; Total Load Y: 203; Total Load B: 147; Total Load N: 55 | 203 | 147 | 15.4004 | OK - No Upgrade | Need to Balance
Masrooq | Al Rob’a AlKhali | K_LN5 | 22.241475, 55.554433 | 1 | Ground (GMT) |  | 500 | 19/05/2026, 12:52 | 1 | 250 | 250 | 251 | 434 | 433 | 434 | 300 mm² |  | 122 | 114 | 93 | 25 | [38 empty] | Total Load R: 122; Total Load Y: 114; Total Load B: 93; Total Load N: 25 | 122 | 93 | 18.3417 | OK - No Upgrade | Need to Balance
Masrooq | Al Rob’a AlKhali | K_LN1 | 22.241475, 55.554433 | 1 | Ground (GMT) |  | 500 | 19/05/2026, 12:53 | 1 | 249 | 250 | 248 | 432 | 430 | 429 | 185 mm² |  | 57 | 104 | 76 | 50 | [38 empty] | Total Load R: 57; Total Load Y: 104; Total Load B: 76; Total Load N: 50 | 104 | 57 | 15.5635 | OK - No Upgrade | Need to Balance
Masrooq | Al Rob’a AlKhali | K_LN1 | 22.241475, 55.554433 | 1 | Ground (GMT) |  | 500 | 11/06/2026, 11:44 | 2 | 245 | 244 | 243 | 424 | 423 | 424 | 240 mm² |  | 103 | 61 | 80 | 46 | [38 empty] | Total Load R: 103; Total Load Y: 61; Total Load B: 80; Total Load N: 46 | 103 | 61 | 15.1284 | OK - No Upgrade | Need to Balance

## AL-ARED
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Feeder 9 | [5 empty] | Feeder 10 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Hijermat | AL-ARED | K_LN5 | 23.375757, 56.590374 | 4622 | Pole (PMT) | 3 | 50 | 08/06/2026, 14:59 | 1 | 235 | 234 | 236 | 405 | 401 | 404 | 185 mm² |  | 8 | 5 | 9 | 3 | [50 empty] | Total Load R: 8; Total Load Y: 5; Total Load B: 9; Total Load N: 3 | 9 | 5 | 12.6267 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.375757, 56.590374 | 1225 | Pole (PMT) | 3 | 100 | 08/06/2026, 14:56 | 1 | 234 | 232 | 232 | 405 | 407 | 406 | [6 empty] | 120 mm² |  | 20 | 44 | 15 | 25 | [44 empty] | Total Load R: 20; Total Load Y: 44; Total Load B: 15; Total Load N: 25 | 44 | 15 | 30.8651 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.375757, 56.590374 | 1224 | Pole (PMT) | 3 | 100 | 08/06/2026, 14:50 | 1 | 234 | 235 | 233 | 406 | 405 | 401 | [6 empty] | 120 mm² |  | 20 | 14 | 10 | 15 | [44 empty] | Total Load R: 20; Total Load Y: 14; Total Load B: 10; Total Load N: 15 | 20 | 10 | 14.0643 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.375757, 56.590374 | 1223 | Pole (PMT) |  | 100 | 08/06/2026, 14:41 | 1 | 233 | 234 | 233 | 408 | 408 | 409 | 120 mm² |  | 27 | 21 | 28 | 4 | [50 empty] | Total Load R: 27; Total Load Y: 21; Total Load B: 28; Total Load N: 4 | 28 | 21 | 19.7869 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.375757, 56.590374 | 1822 | Pole (PMT) | 3 | 100 | 08/06/2026, 14:36 | 1 | 235 | 235 | 234 | 411 | 411 | 408 | 120 mm² |  | 0 | 0 | 0 | 0 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN5 | 23.375757, 56.590374 | 1222 | Pole (PMT) | 3 | 100 | 08/06/2026, 14:34 | 1 | 234 | 234 | 235 | 410 | 410 | 408 | [6 empty] | 120 mm² |  | 30 | 35 | 22 | 25 | [44 empty] | Total Load R: 30; Total Load Y: 35; Total Load B: 22; Total Load N: 25 | 35 | 22 | 24.8549 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.403826, 56.617002 | 1221 | Pole (PMT) |  | 100 | 08/06/2026, 14:29 | 1 | 233 | 233 | 233 | 404 | 485 | 402 | 120 mm² |  | 7 | 18 | 32 | 17 | 120 mm² |  | 14 | 15 | 28 | 16 | [44 empty] | Total Load R: 21; Total Load Y: 33; Total Load B: 60; Total Load N: 33 | 60 | 21 | 41.9849 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.403826, 56.617002 | 1220 | Pole (PMT) | 3 | 100 | 08/06/2026, 14:23 | 1 | 234 | 235 | 234 | 412 | 411 | 412 | 120 mm² |  | 10 | 6 | 8 | 8 | 120 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 10; Total Load Y: 6; Total Load B: 8; Total Load N: 8 | 10 | 6 | 7.136 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.403826, 56.617002 | 2015 | Pole (PMT) | 3 | 100 | 08/06/2026, 14:19 | 1 | 234 | 235 | 234 | 412 | 412 | 410 | 185 mm² |  | 20 | 12 | 8 | 14 | [50 empty] | Total Load R: 20; Total Load Y: 12; Total Load B: 8; Total Load N: 14 | 20 | 8 | 14.2721 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.403826, 56.617002 | 1219 | Pole (PMT) | 5 | 100 | 08/06/2026, 14:16 | 1 | 243 | 242 | 242 | 418 | 418 | 418 | 120 mm² |  | 45 | 17 | 10 | 4 | 185 mm² |  | 20 | 53 | 54 | 17 | [44 empty] | Total Load R: 65; Total Load Y: 70; Total Load B: 64; Total Load N: 21 | 70 | 64 | 50.6798 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN5 | 23.403826, 56.617002 | 1218 | Pole (PMT) | 3 | 315 | 08/06/2026, 14:10 | 1 | 234 | 234 | 235 | 408 | 408 | 408 | 185 mm² |  | 81 | 80 | 32 | 47 | 185 mm² |  | 10 | 8 | 35 | 30 | [44 empty] | Total Load R: 91; Total Load Y: 88; Total Load B: 67; Total Load N: 77 | 91 | 67 | 20.4151 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.403826, 56.617002 | 4659 | Pole (PMT) | 3 | 100 | 08/06/2026, 14:07 | 1 | 236 | 236 | 235 | 412 | 411 | 411 | [6 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN5 | 23.394355, 56.647386 | 4400 | Pole (PMT) | 3 | 100 | 08/06/2026, 14:04 | 1 | 236 | 235 | 236 | 414 | 412 | 412 | 120 mm² |  | 4 | 4 | 6 | 2 | [50 empty] | Total Load R: 4; Total Load Y: 4; Total Load B: 6; Total Load N: 2 | 6 | 4 | 4.3024 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.394355, 56.647386 | 4258 | Pole (PMT) | 3 | 200 | 08/06/2026, 13:56 | 1 | 233 | 233 | 235 | 406 | 406 | 403 | 185 mm² |  | 63 | 96 | 82 | 38 | 185 mm² |  | 6 | 4 | 6 | 2 | [44 empty] | Total Load R: 69; Total Load Y: 100; Total Load B: 88; Total Load N: 40 | 100 | 69 | 35.1606 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.394355, 56.647386 | 4390 | Pole (PMT) | 3 | 100 | 08/06/2026, 13:52 | 1 | 236 | 233 | 232 | 414 | 412 | 413 | 185 mm² |  | 2 | 6 | 6 | 4 | 185 mm² |  | 8 | 10 | 6 | 4 | [44 empty] | Total Load R: 10; Total Load Y: 16; Total Load B: 12; Total Load N: 8 | 16 | 10 | 11.4731 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.394355, 56.647386 | 4563 | Pole (PMT) | 3 | 100 | 08/06/2026, 13:50 | 1 | 236 | 236 | 235 | 414 | 411 | 413 | 185 mm² |  | 8 | 12 | 10 | 6 | [50 empty] | Total Load R: 8; Total Load Y: 12; Total Load B: 10; Total Load N: 6 | 12 | 8 | 8.6048 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.394355, 56.647386 | 4254 | Pole (PMT) | 3 | 100 | 08/06/2026, 13:48 | 1 | 236 | 235 | 236 | 414 | 414 | 413 | 185 mm² |  | 10 | 14 | 8 | 6 | [50 empty] | Total Load R: 10; Total Load Y: 14; Total Load B: 8; Total Load N: 6 | 14 | 8 | 10.039 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.394355, 56.647386 | 4257 | Pole (PMT) | 3 | 100 | 08/06/2026, 13:45 | 1 | 236 | 236 | 237 | 414 | 416 | 414 | 185 mm² |  | 20 | 17 | 22 | 8 | [50 empty] | Total Load R: 20; Total Load Y: 17; Total Load B: 22; Total Load N: 8 | 22 | 17 | 15.7755 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.394355, 56.647386 | 2276 | Pole (PMT) | 3 | 315 | 08/06/2026, 13:42 | 1 | 236 | 236 | 237 | 412 | 412 | 411 | 185 mm² |  | 10 | 12 | 18 | 8 | [50 empty] | Total Load R: 10; Total Load Y: 12; Total Load B: 18; Total Load N: 8 | 18 | 10 | 4.0777 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.394355, 56.647386 | 4308 | Pole (PMT) | 3 | 100 | 08/06/2026, 13:39 | 1 | 238 | 239 | 237 | 416 | 417 | 416 | [6 empty] | 120 mm² |  | 8 | 4 | 6 | 2 | [44 empty] | Total Load R: 8; Total Load Y: 4; Total Load B: 6; Total Load N: 2 | 8 | 4 | 5.7643 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.376468, 56.687716 | 2318 | Pole (PMT) | 3 | 315 | 08/06/2026, 13:26 | 1 | 248 | 249 | 247 | 436 | 435 | 432 | [6 empty] | 185 mm² |  | 114 | 90 | 71 | 45 | [44 empty] | Total Load R: 114; Total Load Y: 90; Total Load B: 71; Total Load N: 45 | 114 | 71 | 27.3301 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.376468, 56.687716 | 1216 | Pole (PMT) | 5 | 315 | 08/06/2026, 13:23 | 1 | 254 | 251 | 253 | 436 | 436 | 435 | 120 mm² |  | 35 | 60 | 50 | 24 | 185 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 35; Total Load Y: 60; Total Load B: 50; Total Load N: 24 | 60 | 35 | 14.3843 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.376468, 56.687716 | 603 | Pole (PMT) | 3 | 100 | 08/06/2026, 13:18 | 1 | 238 | 237 | 238 | 417 | 417 | 417 | 120 mm² |  | 0 | 0 | 0 | 0 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN5 | 23.376452, 56.687674 | 4498 | Pole (PMT) | 3 | 100 | 08/06/2026, 13:16 | 1 | 239 | 238 | 237 | 417 | 417 | 416 | [6 empty] | 185 mm² |  | 8 | 6 | 2 | 2 | [44 empty] | Total Load R: 8; Total Load Y: 6; Total Load B: 2; Total Load N: 2 | 8 | 2 | 5.7781 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.404009, 56.629381 | 1214 | Pole (PMT) | 3 | 315 | 07/06/2026, 14:39 | 1 | 242 | 243 | 243 | 420 | 421 | 419 | 120 mm² |  | 112 | 65 | 58 | 59 | [50 empty] | Total Load R: 112; Total Load Y: 65; Total Load B: 58; Total Load N: 59 | 112 | 58 | 25.8653 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.411878, 56.635088 | 1213 | Pole (PMT) | 3 | 200 | 07/06/2026, 14:30 | 1 | 241 | 242 | 243 | 407 | 418 | 420 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 170 | 152 | 145 | 18 | [44 empty] | Total Load R: 170; Total Load Y: 152; Total Load B: 145; Total Load N: 18 | 170 | 145 | 59.9203 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN5 | 23.411878, 56.635088 | 2067 | Pole (PMT) | 3 | 100 | 07/06/2026, 14:26 | 1 | 231 | 232 | 232 | 400 | 402 | 400 | 120 mm² |  | 16 | 15 | 20 | 13 | [50 empty] | Total Load R: 16; Total Load Y: 15; Total Load B: 20; Total Load N: 13 | 20 | 15 | 13.8564 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.414854, 56.632891 | 1479 | Pole (PMT) | 3 | 315 | 07/06/2026, 14:18 | 1 | 236 | 235 | 236 | 408 | 405 | 408 | 185 mm² |  | 31 | 41 | 44 | 13 | 120 mm² |  | 42 | 35 | 70 | 23 | [44 empty] | Total Load R: 73; Total Load Y: 76; Total Load B: 114; Total Load N: 36 | 114 | 73 | 25.575 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.414954, 56.632776 | 1204 | Pole (PMT) | 3 | 315 | 07/06/2026, 14:13 | 1 | 233 | 235 | 235 | 403 | 407 | 408 | 185 mm² |  | 220 | 134 | 150 | 62 | 185 mm² |  | 68 | 0 | 47 | 52 | [44 empty] | Total Load R: 288; Total Load Y: 134; Total Load B: 197; Total Load N: 114 | 288 | 134 | 63.8186 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.427036, 56.622059 | 1199 | Pole (PMT) | 3 | 315 | 07/06/2026, 14:03 | 1 | 233 | 234 | 233 | 403 | 400 | 402 | 120 mm² |  | 53 | 27 | 48 | 25 | 120 mm² |  | 131 | 173 | 180 | 46 | [44 empty] | Total Load R: 184; Total Load Y: 200; Total Load B: 228; Total Load N: 71 | 228 | 184 | 50.5231 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.426795, 56.622247 | 1200 | Pole (PMT) | 3 | 315 | 07/06/2026, 13:53 | 1 | 250 | 248 | 248 | 432 | 431 | 431 | 120 mm² |  | 60 | 87 | 68 | 35 | 120 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 60; Total Load Y: 87; Total Load B: 68; Total Load N: 35 | 87 | 60 | 20.6658 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.425335, 56.622018 | 1873 | Pole (PMT) | 3 | 315 | 07/06/2026, 13:49 | 1 | 234 | 236 | 237 | 404 | 408 | 407 | 120 mm² |  | 182 | 196 | 131 | 66 | 120 mm² |  | 204 | 106 | 161 | 82 | [44 empty] | Total Load R: 386; Total Load Y: 302; Total Load B: 292; Total Load N: 148 | 386 | 292 | 85.747 | Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.423651, 56.612781 | 1521 | Pole (PMT) | 3 | 100 | 07/06/2026, 13:43 | 1 | 241 | 236 | 240 | 415 | 417 | 407 | 185 mm² |  | 54 | 134 | 52 | 70 | [50 empty] | Total Load R: 54; Total Load Y: 134; Total Load B: 52; Total Load N: 70 | 134 | 52 | 96.3193 | Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.420835, 56.629472 | 1581 | Pole (PMT) | 5 | 315 | 07/06/2026, 13:39 | 1 | 245 | 244 | 244 | 423 | 423 | 423 | 185 mm² |  | 149 | 138 | 127 | 18 | 185 mm² |  | 40 | 26 | 16 | 21 | [44 empty] | Total Load R: 189; Total Load Y: 164; Total Load B: 143; Total Load N: 39 | 189 | 143 | 43.9594 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.420835, 56.629472 | 1201 | Ground (GMT) | 3 | 1000 | 07/06/2026, 13:33 | 1 | 236 | 236 | 235 | 408 | 409 | 407 | [18 empty] | 185 mm² |  | 83 | 48 | 55 | 26 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 30 | 0 | 32 | 25 | [20 empty] | Total Load R: 113; Total Load Y: 48; Total Load B: 87; Total Load N: 51 | 113 | 48 | 7.9854 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.420816, 56.629889 | 1203 | Pole (PMT) |  | 315 | 07/06/2026, 13:18 | 1 | 238 | 237 | 238 | 412 | 413 | 412 | 120 mm² |  | 22 | 52 | 58 | 36 | 120 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 22; Total Load Y: 52; Total Load B: 58; Total Load N: 36 | 58 | 22 | 13.1394 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.420909, 56.629212 | 2369 | Pole (PMT) | 3 | 315 | 07/06/2026, 13:15 | 1 | 238 | 239 | 238 | 413 | 414 | 414 | 185 mm² |  | 18 | 20 | 22 | 0 | 70 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 18; Total Load Y: 20; Total Load B: 22; Total Load N: 0 | 22 | 18 | 4.996 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN5 | 23.42077, 56.632243 | 1208 | Ground (GMT) | 3 | 500 | 07/06/2026, 13:08 | 1 | 239 | 239 | 240 | 413 | 417 | 415 | 185 mm² |  | 138 | 108 | 151 | 36 | 185 mm² |  | 53 | 22 | 11 | 37 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 191; Total Load Y: 130; Total Load B: 162; Total Load N: 73 | 191 | 130 | 27.3259 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.42077, 56.632243 | 1207 | Pole (PMT) | 3 | 100 | 07/06/2026, 13:01 | 1 | 227 | 227 | 228 | 383 | 383 | 386 | 120 mm² |  | 12 | 0 | 14 | 14 | 70 mm² |  | 16 | 0 | 0 | 14 | [44 empty] | Total Load R: 28; Total Load Y: 0; Total Load B: 14; Total Load N: 28 | 28 | 0 | 18.5745 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.42077, 56.632243 | 1206 | Pole (PMT) | 3 | 315 | 07/06/2026, 12:57 | 1 | 236 | 235 | 238 | 406 | 402 | 408 | 120 mm² |  | 65 | 58 | 67 | 10 | 185 mm² |  | 148 | 115 | 54 | 70 | [44 empty] | Total Load R: 213; Total Load Y: 173; Total Load B: 121; Total Load N: 80 | 213 | 121 | 47.5506 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.416033, 56.638007 | 1205 | Pole (PMT) | 3 | 315 | 07/06/2026, 12:48 | 1 | 235 | 234 | 236 | 404 | 408 | 409 | 185 mm² |  | 37 | 0 | 23 | 31 | 185 mm² |  | 184 | 129 | 124 | 53 | [44 empty] | Total Load R: 221; Total Load Y: 129; Total Load B: 147; Total Load N: 84 | 221 | 129 | 49.0935 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.413572, 56.636271 | 1686 | Ground (GMT) | 3 | 1000 | 07/06/2026, 12:39 | 1 | 238 | 237 | 239 | 411 | 413 | 412 | 185 mm² |  | 36 | 22 | 48 | 21 | 185 mm² |  | 11 | 57 | 20 | 33 | [44 empty] | Total Load R: 47; Total Load Y: 79; Total Load B: 68; Total Load N: 54 | 79 | 47 | 5.6238 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.422519, 56.627132 | 1803 | Pole (PMT) |  | 100 | 01/06/2026, 15:24 | 1 | 243 | 242 | 242 | 420 | 422 | 423 | 120 mm² |  | 0 | 0 | 0 | 0 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN4 | 23.439634, 56.611862 | 1510 | Pole (PMT) |  | 100 | 01/06/2026, 15:16 | 1 | 244 | 243 | 224 | 423 | 426 | 423 | 120 mm² |  | 0 | 0 | 0 | 0 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN4 | 23.439572, 56.611737 | 1196 | Pole (PMT) |  | 100 | 01/06/2026, 15:11 | 1 | 242 | 241 | 240 | 424 | 421 | 424 | 120 mm² |  | 0 | 0 | 4 | 0 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 4; Total Load N: 0 | 4 | 0 | 2.9376 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.439572, 56.611737 | 1195 | Pole (PMT) |  | 100 | 01/06/2026, 15:09 | 1 | 240 | 241 | 241 | 419 | 420 | 419 | 120 mm² |  | 2 | 4 | 8 | 2 | [50 empty] | Total Load R: 2; Total Load Y: 4; Total Load B: 8; Total Load N: 2 | 8 | 2 | 5.8058 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.439597, 56.611761 | 1194 | Pole (PMT) |  | 100 | 01/06/2026, 15:08 | 1 | 243 | 242 | 241 | 420 | 420 | 420 | 185 mm² |  | 21 | 10 | 44 | 29 | [50 empty] | Total Load R: 21; Total Load Y: 10; Total Load B: 44; Total Load N: 29 | 44 | 10 | 32.0083 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.439583, 56.611752 | 1193 | Pole (PMT) |  | 315 | 01/06/2026, 15:07 | 1 | 240 | 242 | 240 | 422 | 420 | 421 | 120 mm² |  | 23 | 117 | 69 | 84 | [50 empty] | Total Load R: 23; Total Load Y: 117; Total Load B: 69; Total Load N: 84 | 117 | 23 | 27.1487 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.439595, 56.611769 | 1192 | Pole (PMT) |  | 315 | 01/06/2026, 15:05 | 1 | 241 | 241 | 241 | 419 | 420 | 419 | [6 empty] | 120 mm² |  | 104 | 50 | 122 | 64 | [44 empty] | Total Load R: 104; Total Load Y: 50; Total Load B: 122; Total Load N: 64 | 122 | 50 | 28.1076 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.439576, 56.611847 | 4324 | Pole (PMT) |  | 100 | 01/06/2026, 15:03 | 1 | 240 | 241 | 210 | 420 | 419 | 419 | 120 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN4 | 23.441268, 56.614022 | 1191 | Pole (PMT) |  | 315 | 01/06/2026, 14:40 | 1 | 242 | 242 | 243 | 419 | 418 | 420 | 185 mm² |  | 117 | 40 | 137 | 85 | 120 mm² |  | 38 | 44 | 23 | 12 | [44 empty] | Total Load R: 155; Total Load Y: 84; Total Load B: 160; Total Load N: 97 | 160 | 84 | 36.8624 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.438542, 56.61748 | 1190 | Pole (PMT) |  | 315 | 01/06/2026, 14:35 | 1 | 232 | 231 | 231 | 403 | 403 | 401 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 145 | 108 | 137 | 41 | [44 empty] | Total Load R: 145; Total Load Y: 108; Total Load B: 137; Total Load N: 41 | 145 | 108 | 32.1309 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.440905, 56.621694 | 2349 | Pole (PMT) |  | 315 | 01/06/2026, 14:31 | 1 | 244 | 245 | 243 | 420 | 421 | 421 | 185 mm² |  | 10 | 50 | 10 | 40 | 185 mm² |  | 77 | 68 | 60 | 14 | [44 empty] | Total Load R: 87; Total Load Y: 118; Total Load B: 70; Total Load N: 54 | 118 | 70 | 27.2509 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.440093, 56.624749 | 1189 | Pole (PMT) |  | 315 | 01/06/2026, 14:28 | 1 | 241 | 240 | 239 | 416 | 417 | 416 | 185 mm² |  | 70 | 20 | 31 | 37 | 120 mm² |  | 195 | 206 | 124 | 50 | 185 mm² |  | 48 | 60 | 40 | 21 | [38 empty] | Total Load R: 313; Total Load Y: 286; Total Load B: 195; Total Load N: 108 | 313 | 195 | 71.5958 | Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.356269, 56.566319 | 2107 | Pole (PMT) |  | 315 | 01/06/2026, 14:19 | 1 | 242 | 243 | 240 | 422 | 423 | 421 | 185 mm² |  | 90 | 80 | 83 | 11 | 185 mm² |  | 58 | 61 | 40 | 16 | [44 empty] | Total Load R: 148; Total Load Y: 141; Total Load B: 123; Total Load N: 27 | 148 | 123 | 34.3419 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN4 | 23.252571, 56.538031 | 1197 | Pole (PMT) |  | 315 | 01/06/2026, 14:12 | 1 | 212 | 242 | 242 | 420 | 421 | 421 | 185 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 36 | 42 | 15 | 27 | [44 empty] | Total Load R: 36; Total Load Y: 42; Total Load B: 15; Total Load N: 27 | 42 | 15 | 9.6995 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.5, 57.5 | 1198 | Ground (GMT) |  | 1000 | 01/06/2026, 14:03 | 1 | 242 | 243 | 242 | 420 | 421 | 419 | 120 mm² | [11 empty] | 120 mm² |  | 285 | 288 | 187 | 85 | 120 mm² |  | 51 | 48 | 60 | 13 | [12 empty] | 185 mm² |  | 105 | 126 | 64 | 66 | 185 mm² |  | 0 | 0 | 0 | 0 | [8 empty] | Total Load R: 441; Total Load Y: 462; Total Load B: 311; Total Load N: 164 | 462 | 311 | 33.6087 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.5, 57.5 | 1209 | Ground (GMT) |  | 1000 | 01/06/2026, 13:58 | 1 | 244 | 245 | 244 | 421 | 420 | 421 | 185 mm² |  | 10 | 34 | 15 | 28 | [6 empty] | 120 mm² |  | 98 | 89 | 118 | 32 | 120 mm² |  | 62 | 80 | 20 | 38 | [6 empty] | 120 mm² |  | 37 | 58 | 16 | 18 | 120 mm² |  | 73 | 65 | 90 | 36 | 185 mm² |  | 64 | 24 | 15 | 40 | [8 empty] | Total Load R: 344; Total Load Y: 350; Total Load B: 274; Total Load N: 192 | 350 | 274 | 25.5218 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN4 | 23.5, 57.5 | 1187 | Ground (GMT) |  | 1000 | 01/06/2026, 13:51 | 1 | 238 | 239 | 210 | 412 | 413 | 413 | 70 mm² |  | 13 | 35 | 10 | 23 | 120 mm² |  | 38 | 80 | 33 | 38 | 185 mm² |  | 218 | 220 | 217 | 23 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 5 | 4 | 4 | 9 | [26 empty] | Total Load R: 274; Total Load Y: 339; Total Load B: 264; Total Load N: 93 | 339 | 264 | 24.1912 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN5 | 23.5, 57.5 | 1202 | Ground (GMT) |  | 1000 | 01/06/2026, 13:42 | 1 | 239 | 239 | 240 | 415 | 416 | 417 | 185 mm² |  | 71 | 90 | 89 | 17 | 185 mm² |  | 80 | 50 | 66 | 18 | 185 mm² |  | 33 | 30 | 20 | 13 | 185 mm² |  | 109 | 98 | 34 | 57 | [32 empty] | Total Load R: 293; Total Load Y: 268; Total Load B: 209; Total Load N: 105 | 293 | 209 | 21.0609 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.495297, 57.470531 | 1210 | Ground (GMT) |  | 1000 | 01/06/2026, 13:36 | 1 | 246 | 244 | 245 | 435 | 426 | 426 | 185 mm² |  | 34 | 49 | 63 | 22 | 120 mm² |  | 26 | 28 | 66 | 30 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 63 | 81 | 165 | 30 | 120 mm² |  | 61 | 74 | 98 | 36 | 185 mm² |  | 120 | 118 | 70 | 51 | [20 empty] | Total Load R: 304; Total Load Y: 350; Total Load B: 462; Total Load N: 169 | 462 | 304 | 34.809 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.5, 57.5 | 1183 | Pole (PMT) |  | 315 | 01/06/2026, 13:29 | 1 | 246 | 244 | 248 | 427 | 430 | 429 | 185 mm² |  | 40 | 15 | 17 | 26 |  |  | 26 | 26 | 52 | 20 | [44 empty] | Total Load R: 66; Total Load Y: 41; Total Load B: 69; Total Load N: 46 | 69 | 41 | 16.2004 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.5, 57.5 | 1184 | Pole (PMT) |  | 100 | 01/06/2026, 13:25 | 1 | 247 | 249 | 250 | 431 | 433 | 433 | 120 mm² |  | 18 | 0 | 8 | 9 | [50 empty] | Total Load R: 18; Total Load Y: 0; Total Load B: 8; Total Load N: 9 | 18 | 0 | 13.4373 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN4 | 23.5, 57.5 | 1182 | Pole (PMT) |  | 315 | 01/06/2026, 13:22 | 1 | 246 | 245 | 248 | 427 | 4230 | 424 | 185 mm² |  | 27 | 15 | 25 | 17 | 185 mm² |  | 189 | 155 | 126 | 41 | [44 empty] | Total Load R: 216; Total Load Y: 170; Total Load B: 151; Total Load N: 58 | 216 | 151 | 50.7144 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.44823, 56.637189 | 2047 | Ground (GMT) |  | 1000 | 21/05/2026, 14:59 | 1 | 245 | 244 | 244 | 425 | 427 | 426 | [24 empty] | 185 mm² |  | 0 | 24 | 13 | 16 | 185 mm² |  | 45 | 52 | 35 | 32 | 185 mm² |  | 57 | 54 | 74 | 22 | 185 mm² |  | 49 | 44 | 17 | 18 | [8 empty] | Total Load R: 151; Total Load Y: 174; Total Load B: 139; Total Load N: 88 | 174 | 139 | 12.8085 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.448169, 56.639704 | 1413 | Pole (PMT) |  | 100 | 21/05/2026, 14:53 | 1 | 243 | 243 | 244 | 418 | 419 | 423 | 185 mm² |  | 0 | 22 | 0 | 12 | 185 mm² |  | 79 | 51 | 40 | 25 | [44 empty] | Total Load R: 79; Total Load Y: 73; Total Load B: 40; Total Load N: 37 | 79 | 40 | 57.1958 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.44752, 56.642406 | 1226 | Pole (PMT) |  | 315 | 21/05/2026, 14:49 | 1 | 245 | 244 | 244 | 424 | 424 | 427 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 25 | 13 | 0 | 21 | [44 empty] | Total Load R: 25; Total Load Y: 13; Total Load B: 0; Total Load N: 21 | 25 | 0 | 5.8285 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.473803, 56.648219 | 2152 | Pole (PMT) |  | 315 | 21/05/2026, 14:41 | 1 | 240 | 240 | 241 | 416 | 417 | 416 | [18 empty] | 185 mm² |  | 0 | 0 | 12 | 12 | [32 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 12; Total Load N: 12 | 12 | 0 | 2.7449 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.477783, 56.646593 | 2322 | Pole (PMT) |  | 100 | 21/05/2026, 14:36 | 1 | 240 | 240 | 242 | 417 | 416 | 417 | 70 mm² |  | 0 | 0 | 0 | 0 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN3 | 23.480013, 56.641074 | 1241 | Pole (PMT) |  | 315 | 21/05/2026, 14:33 | 1 | 237 | 236 | 238 | 412 | 413 | 412 | 120 mm² |  | 131 | 147 | 120 | 0 | 120 mm² |  | 38 | 31 | 26 | 11 | [44 empty] | Total Load R: 169; Total Load Y: 178; Total Load B: 146; Total Load N: 11 | 178 | 146 | 40.3243 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN3 | 23.48404, 56.637406 | 1242 | Pole (PMT) |  | 200 | 21/05/2026, 14:29 | 1 | 237 | 238 | 237 | 412 | 413 | 412 | 120 mm² |  | 66 | 51 | 59 | 24 | [50 empty] | Total Load R: 66; Total Load Y: 51; Total Load B: 59; Total Load N: 24 | 66 | 51 | 23.549 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.468895, 56.654902 | 2166 | Pole (PMT) |  | 315 | 21/05/2026, 14:21 | 1 | 239 | 239 | 234 | 416 | 415 | 416 | 240 mm² |  | 74 | 47 | 44 | 31 | 240 mm² |  | 0 | 16 | 38 | 19 | [44 empty] | Total Load R: 74; Total Load Y: 63; Total Load B: 82; Total Load N: 50 | 82 | 63 | 18.7567 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.466899, 56.655862 | 1239 | Pole (PMT) |  | 315 | 21/05/2026, 14:13 | 1 | 247 | 249 | 278 | 429 | 430 | 427 | 120 mm² |  | 57 | 16 | 27 | 33 | 120 mm² |  | 177 | 159 | 281 | 74 | [44 empty] | Total Load R: 234; Total Load Y: 175; Total Load B: 308; Total Load N: 107 | 308 | 175 | 72.6538 | Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.460382, 56.658466 | 01147 | Ground (GMT) |  | 1000 | 21/05/2026, 13:59 | 1 | 242 | 241 | 241 | 418 | 419 | 420 | 185 mm² |  | 0 | 62 | 16 | 46 | 185 mm² |  | 271 | 195 | 196 | 55 | 185 mm² |  | 21 | 15 | 13 | 0 | 185 mm² |  | 13 | 0 | 10 | 0 | [32 empty] | Total Load R: 305; Total Load Y: 272; Total Load B: 235; Total Load N: 101 | 305 | 235 | 22.0819 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.457702, 56.660464 | 2151 | Pole (PMT) |  | 315 | 21/05/2026, 13:53 | 1 | 238 | 239 | 238 | 414 | 414 | 416 | 185 mm² |  | 13 | 23 | 27 | 10 | 185 mm² |  | 116 | 66 | 136 | 43 | [44 empty] | Total Load R: 129; Total Load Y: 89; Total Load B: 163; Total Load N: 53 | 163 | 89 | 37.1055 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.453286, 56.66199 | 1229 | Pole (PMT) |  | 100 | 21/05/2026, 13:46 | 1 | 235 | 235 | 236 | 407 | 408 | 407 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN1 | 23.447336, 56.627494 | 1249 | Ground (GMT) |  | 1000 | 21/05/2026, 09:41 | 1 | 244 | 243 | 244 | 423 | 424 | 422 | 300 mm² |  | 300 | 220 | 210 | 8 | 300 mm² |  | 90 | 80 | 78 | 10 | 240 mm² |  | 90 | 70 | 94 | 3 | 240 mm² |  | 34 | 33 | 34 | 2 | 300 mm² |  | 270 | 270 | 220 | 8 | [26 empty] | Total Load R: 784; Total Load Y: 673; Total Load B: 636; Total Load N: 31 | 784 | 636 | 57.4403 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.490414, 56.646474 | 1660 | Ground (GMT) |  | 500 | 20/05/2026, 15:10 | 1 | 239 | 238 | 210 | 416 | 416 | 416 | 185 mm² |  | 10 | 10 | 10 | 9 | 185 mm² |  | 76 | 55 | 35 | 29 | 185 mm² |  | 8 | 6 | 5 | 5 |  |  | 20 | 18 | 15 | 8 | [32 empty] | Total Load R: 114; Total Load Y: 89; Total Load B: 65; Total Load N: 51 | 114 | 65 | 16.4282 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.486618, 56.649182 | 2169 | Pole (PMT) |  | 315 | 20/05/2026, 14:50 | 1 | 239 | 239 | 240 | 416 | 416 | 417 | 185 mm² |  | 52 | 59 | 49 | 12 | [50 empty] | Total Load R: 52; Total Load Y: 59; Total Load B: 49; Total Load N: 12 | 59 | 49 | 13.4957 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.485716, 56.657836 | 1246 | Pole (PMT) |  | 315 | 20/05/2026, 15:00 | 1 | 239 | 239 | 238 | 417 | 418 | 418 | 120 mm² |  | 45 | 63 | 158 | 95 | 185 mm² |  | 12 | 10 | 8 | 3 | [44 empty] | Total Load R: 57; Total Load Y: 73; Total Load B: 166; Total Load N: 98 | 166 | 57 | 38.0622 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.483472, 56.654029 | 1248 | Pole (PMT) |  | 315 | 20/05/2026, 15:00 | 1 | 238 | 236 | 237 | 410 | 413 | 411 | 120 mm² |  | 94 | 95 | 55 | 44 | 120 mm² |  | 10 | 24 | 15 | 20 | [44 empty] | Total Load R: 104; Total Load Y: 119; Total Load B: 70; Total Load N: 64 | 119 | 70 | 26.8275 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.473744, 56.652179 | 1240 | Pole (PMT) |  | 100 | 20/05/2026, 14:59 | 1 | 238 | 238 | 239 | 417 | 417 | 416 | 120 mm² |  | 0 | 0 | 0 | 0 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN3 | 23.474546, 56.655063 | 1243 | Pole (PMT) |  | 315 | 20/05/2026, 14:59 | 1 | 233 | 233 | 236 | 404 | 408 | 409 | 120 mm² |  | 65 | 76 | 27 | 45 | 185 mm² |  | 20 | 29 | 20 | 6 | [44 empty] | Total Load R: 85; Total Load Y: 105; Total Load B: 47; Total Load N: 51 | 105 | 47 | 23.325 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.474752, 56.6574 | 1244 | Ground (GMT) |  | 1000 | 20/05/2026, 14:52 | 1 | 238 | 239 | 240 | 413 | 414 | 413 | 185 mm² |  | 80 | 91 | 85 | 18 |  |  | 63 | 49 | 61 | 10 |  |  | 80 | 60 | 78 | 14 |  |  | 80 | 72 | 89 | 16 | [32 empty] | Total Load R: 303; Total Load Y: 272; Total Load B: 313; Total Load N: 58 | 313 | 272 | 22.39 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN3 | 23.475582, 56.658475 | 2221 | Pole (PMT) |  | 315 | 20/05/2026, 14:58 | 1 | 238 | 238 | 239 | 414 | 416 | 413 | 185 mm² |  | 53 | 30 | 20 | 46 | 185 mm² |  | 22 | 19 | 13 | 13 | [44 empty] | Total Load R: 75; Total Load Y: 49; Total Load B: 33; Total Load N: 59 | 75 | 33 | 17.0731 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.47189, 56.662023 | 1245 | Pole (PMT) |  | 315 | 20/05/2026, 14:58 | 1 | 237 | 238 | 238 | 412 | 410 | 412 | 185 mm² |  | 102 | 95 | 145 | 22 |  |  | 13 | 11 | 11 | 5 | [44 empty] | Total Load R: 115; Total Load Y: 106; Total Load B: 156; Total Load N: 27 | 156 | 106 | 35.3404 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.489851, 56.672164 | 1895 | Pole (PMT) |  | 100 | 20/05/2026, 14:57 | 1 | 239 | 239 | 240 | 418 | 418 | 417 | 120 mm² |  | 0 | 0 | 0 | 0 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN3 | 23.486333, 56.672459 | 1496 | Pole (PMT) |  | 100 | 20/05/2026, 14:57 | 1 | 239 | 239 | 240 | 417 | 416 | 416 | 120 mm² |  | 0 | 0 | 0 | 0 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN3 | 23.484955, 56.670698 | 4133 | Pole (PMT) |  | 315 | 20/05/2026, 14:55 | 1 | 239 | 239 | 240 | 419 | 418 | 419 | 185 mm² |  | 28 | 20 | 8 | 15 | [50 empty] | Total Load R: 28; Total Load Y: 20; Total Load B: 8; Total Load N: 15 | 28 | 8 | 6.4509 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.480261, 56.670035 | 4770 | Pole (PMT) |  | 100 | 20/05/2026, 14:55 | 1 | 241 | 240 | 239 | 418 | 3419 | 421 | 185 mm² |  | 0 | 0 | 0 | 0 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN3 | 23.475811, 56.668733 | 1236 | Pole (PMT) |  | 100 | 20/05/2026, 14:55 | 1 | 240 | 239 | 241 | 416 | 418 | 416 | 120 mm² |  | 18 | 38 | 27 | 21 |  |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 18; Total Load Y: 38; Total Load B: 27; Total Load N: 21 | 38 | 18 | 27.3803 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.467808, 56.667969 | 4134 | Pole (PMT) |  | 315 | 20/05/2026, 14:54 | 1 | 240 | 239 | 241 | 420 | 419 | 419 | 185 mm² |  | 12 | 14 | 13 | 10 | [50 empty] | Total Load R: 12; Total Load Y: 14; Total Load B: 13; Total Load N: 10 | 14 | 12 | 3.2332 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN3 | 23.467844, 56.667945 | 4642 | Pole (PMT) |  | 100 | 20/05/2026, 14:54 | 1 | 241 | 241 | 243 | 422 | 421 | 418 | 185 mm² |  | 0 | 0 | 0 | 0 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN3 | 23.469693, 56.672765 | 1235 | Pole (PMT) |  | 100 | 20/05/2026, 14:54 | 1 | 240 | 239 | 240 | 421 | 422 | 421 | 120 mm² |  | 3 | 5 | 8 | 4 | [50 empty] | Total Load R: 3; Total Load Y: 5; Total Load B: 8; Total Load N: 4 | 8 | 3 | 5.8335 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.469637, 56.672912 | 1820 | Pole (PMT) |  | 100 | 20/05/2026, 14:53 | 1 | 240 | 239 | 240 | 424 | 423 | 424 | 185 mm² |  | 42 | 51 | 54 | 12 | 185 mm² |  | 12 | 23 | 14 | 8 | [44 empty] | Total Load R: 54; Total Load Y: 74; Total Load B: 68; Total Load N: 20 | 74 | 54 | 54.3448 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.467275, 56.67794 | 1234 | Pole (PMT) |  | 315 | 20/05/2026, 14:53 | 1 | 240 | 241 | 242 | 420 | 420 | 417 | 120 mm² |  | 105 | 81 | 75 | 28 | 120 mm² |  | 53 | 18 | 43 | 42 | [44 empty] | Total Load R: 158; Total Load Y: 99; Total Load B: 118; Total Load N: 70 | 158 | 99 | 36.4885 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.469175, 56.679085 | 1238 | Pole (PMT) |  | 315 | 20/05/2026, 14:52 | 1 | 242 | 243 | 241 | 442 | 445 | 441 | 120 mm² |  | 30 | 20 | 34 | 33 | 120 mm² |  | 75 | 76 | 88 | 14 | [44 empty] | Total Load R: 105; Total Load Y: 96; Total Load B: 122; Total Load N: 47 | 122 | 96 | 29.6505 | OK - No Upgrade | Need to Balance
Hijermat | AL-ARED | K_LN3 | 23.466114, 56.678509 | 1237 | Pole (PMT) |  | 315 | 20/05/2026, 14:52 | 1 | 243 | 244 | 246 | 424 | 424 | 423 | 120 mm² |  | 60 | 57 | 48 | 13 | [50 empty] | Total Load R: 60; Total Load Y: 57; Total Load B: 48; Total Load N: 13 | 60 | 48 | 13.9884 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN4 | 23.39346, 56.717661 | 1186 | Ground (GMT) |  | 500 | 21/05/2026, 08:51 | 1 | 236 | 236 | 237 | 408 | 410 | 412 | 185 mm² |  | 104 | 112 | 125 | 84 |  |  | 110 | 120 | 72 | 26 | [44 empty] | Total Load R: 214; Total Load Y: 232; Total Load B: 197; Total Load N: 110 | 232 | 197 | 32.7898 | OK - No Upgrade | OK - Balanced
Hijermat | AL-ARED | K_LN4 | 23.39346, 56.717661 | 1185 | Ground (GMT) |  | 1000 | 20/05/2026, 11:58 | 1 | 245 | 249 | 246 | 428 | 431 | 439 | 185 mm² |  | 125 | 90 | 71 | 45 |  |  | 45 | 45 | 45 | 38 |  |  | 114 | 157 | 106 | 41 | [8 empty] | 10 |  |  | 10 | [26 empty] | Total Load R: 294; Total Load Y: 292; Total Load B: 222; Total Load N: 134 | 294 | 222 | 21.7947 | OK - No Upgrade | OK - Balanced

## MAQNYAT
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Feeder 9 | [5 empty] | Feeder 10 | [5 empty] | Feeder 11 | [5 empty] | Feeder 12 | [5 empty] | Feeder 13 | [5 empty] | Feeder 14 | [5 empty] | Feeder 15 | [5 empty] | Feeder 16 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Hijermat | MAQNYAT | K_LN7 | 23.379604, 56.89729 | 1458 | Pole (PMT) | 3 | 100 | 04/06/2026, 15:24 | 1 | 229 | 232 | 230 | 396 | 400 | 399 | 120 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN7 | 23.376925, 56.893607 | 2222 | Ground (GMT) | 3 | 1000 | 04/06/2026, 15:15 | 1 | 226 | 228 | 226 | 392 | 394 | 392 | 185 mm² |  | 40 | 20 | 9 | 30 | 185 mm² |  | 95 | 50 | 93 | 45 | 185 mm² |  | 34 | 15 | 22 | 15 | 185 mm² |  | 17 | 40 | 32 | 25 | [68 empty] | Total Load R: 186; Total Load Y: 125; Total Load B: 156; Total Load N: 115 | 186 | 125 | 12.6287 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.375108, 56.893042 | 1114 | Pole (PMT) | 3 | 315 | 04/06/2026, 15:09 | 1 | 236 | 240 | 236 | 405 | 415 | 411 | 120 mm² |  | 86 | 70 | 160 | 81 | 120 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 70 | 35 | 44 | 66 | [74 empty] | Total Load R: 156; Total Load Y: 105; Total Load B: 204; Total Load N: 147 | 204 | 105 | 45.4292 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.371068, 56.891592 | 4746 | Ground (GMT) | 3 | 1000 | 04/06/2026, 15:00 | 1 | 226 | 230 | 227 | 392 | 395 | 394 | 185 mm² |  | 78 | 25 | 97 | 62 | 185 mm² |  | 52 | 27 | 34 | 24 | 185 mm² |  | 171 | 81 | 116 | 80 | [74 empty] | Total Load R: 301; Total Load Y: 133; Total Load B: 247; Total Load N: 166 | 301 | 133 | 20.4368 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.372763, 56.888374 | 1109 | Ground (GMT) | 3 | 500 | 04/06/2026, 14:53 | 1 | 226 | 229 | 228 | 391 | 396 | 393 | [18 empty] | 185 mm² |  | 80 | 75 | 86 | 51 | 185 mm² |  | 22 | 31 | 29 | 22 | 185 mm² |  | 128 | 73 | 80 | 58 | [56 empty] | Total Load R: 230; Total Load Y: 179; Total Load B: 195; Total Load N: 131 | 230 | 179 | 31.1527 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.3718, 56.887132 | 1110 | Ground (GMT) | 5 | 1000 | 04/06/2026, 14:46 | 1 | 237 | 241 | 240 | 412 | 418 | 417 | [12 empty] | 185 mm² |  | 61 | 33 | 115 | 46 | 185 mm² |  | 25 | 59 | 83 | 40 | 120 mm² |  | 28 | 36 | 23 | 12 | 120 mm² |  | 210 | 102 | 98 | 110 | 185 mm² |  | 215 | 166 | 170 | 63 | 120 mm² |  | 65 | 94 | 28 | 61 | [44 empty] | Total Load R: 604; Total Load Y: 490; Total Load B: 517; Total Load N: 332 | 604 | 490 | 43.1017 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.369281, 56.886355 | 2023 | Pole (PMT) | 3 | 315 | 04/06/2026, 14:37 | 1 | 229 | 228 | 230 | 398 | 396 | 395 | 185 mm² |  | 58 | 56 | 87 | 23 | 185 mm² |  | 91 | 55 | 42 | 47 | [80 empty] | Total Load R: 149; Total Load Y: 111; Total Load B: 129; Total Load N: 70 | 149 | 111 | 32.6076 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.367247, 56.885747 | 1112 | Pole (PMT) | 3 | 315 | 04/06/2026, 14:31 | 1 | 224 | 227 | 226 | 389 | 394 | 389 | 120 mm² |  | 223 | 139 | 209 | 82 | 120 mm² |  | 19 | 33 | 55 | 29 | [80 empty] | Total Load R: 242; Total Load Y: 172; Total Load B: 264; Total Load N: 111 | 264 | 172 | 56.4682 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.370437, 56.886023 | 1111 | Pole (PMT) | 3 | 315 | 04/06/2026, 14:27 | 1 | 226 | 224 | 229 | 393 | 397 | 394 | 120 mm² |  | 27 | 18 | 75 | 67 | 120 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 143 | 69 | 39 | 82 | [74 empty] | Total Load R: 170; Total Load Y: 87; Total Load B: 114; Total Load N: 149 | 170 | 87 | 36.736 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.375625, 56.882098 | 1108 | Pole (PMT) | 3 | 200 | 04/06/2026, 14:20 | 1 | 243 | 246 | 244 | 420 | 426 | 422 | 120 mm² |  | 6 | 3 | 39 | 26 | 120 mm² |  | 65 | 7 | 3 | 48 | [80 empty] | Total Load R: 71; Total Load Y: 10; Total Load B: 42; Total Load N: 74 | 71 | 10 | 25.8249 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.375607, 56.882137 | 1106 | Pole (PMT) | 3 | 200 | 04/06/2026, 14:13 | 1 | 233 | 235 | 235 | 405 | 406 | 404 | 120 mm² |  | 39 | 7 | 25 | 36 | 120 mm² |  | 13 | 29 | 5 | 22 | [80 empty] | Total Load R: 52; Total Load Y: 36; Total Load B: 30; Total Load N: 58 | 52 | 30 | 18.2385 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.37409, 56.883407 | 4527 | Pole (PMT) | 3 | 315 | 04/06/2026, 14:09 | 1 | 234 | 235 | 235 | 405 | 407 | 406 | 185 mm² |  | 15 | 14 | 16 | 5 | 185 mm² |  | 3 | 36 | 12 | 28 | [80 empty] | Total Load R: 18; Total Load Y: 50; Total Load B: 28; Total Load N: 33 | 50 | 18 | 11.1346 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.377573, 56.877542 | 1104 | Pole (PMT) | 3 | 315 | 04/06/2026, 14:04 | 1 | 238 | 239 | 239 | 413 | 412 | 413 | 120 mm² |  | 0 | 3 | 0 | 1 | [86 empty] | Total Load R: 0; Total Load Y: 3; Total Load B: 0; Total Load N: 1 | 3 | 0 | 0.68127 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.375323, 56.871193 | 1103 | Pole (PMT) | 3 | 100 | 04/06/2026, 13:59 | 1 | 235 | 236 | 237 | 411 | 409 | 408 | 120 mm² |  | 50 | 35 | 29 | 25 | [86 empty] | Total Load R: 50; Total Load Y: 35; Total Load B: 29; Total Load N: 25 | 50 | 29 | 35.5936 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.377859, 56.87042 | 600 | Pole (PMT) | 3 | 100 | 04/06/2026, 13:55 | 1 | 238 | 239 | 237 | 411 | 412 | 411 | 50 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN7 | 23.37868, 56.870687 | 1668 | Ground (GMT) | 3 | 500 | 04/06/2026, 13:53 | 1 | 240 | 241 | 241 | 418 | 417 | 417 | 240 mm² |  | 18 | 35 | 15 | 23 | 240 mm² |  | 18 | 38 | 35 | 12 | [12 empty] | 70 mm² |  | 0 | 12 | 11 | 12 | 70 mm² |  | 0 | 0 | 0 | 0 | [56 empty] | Total Load R: 36; Total Load Y: 85; Total Load B: 61; Total Load N: 47 | 85 | 36 | 12.308 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.378679, 56.87069 | 1102 | Pole (PMT) | 3 | 315 | 04/06/2026, 13:47 | 1 | 238 | 238 | 238 | 412 | 413 | 411 | 185 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 10 | 4 | 7 | 3 | [74 empty] | Total Load R: 10; Total Load Y: 4; Total Load B: 7; Total Load N: 3 | 10 | 4 | 2.2654 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.37809, 56.877575 | 4599 | Pole (PMT) | 3 | 100 | 04/06/2026, 13:39 | 1 | 237 | 237 | 238 | 412 | 411 | 411 | 120 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN7 | 23.378911, 56.876335 | 1105 | Pole (PMT) | 3 | 315 | 04/06/2026, 13:34 | 1 | 237 | 238 | 238 | 412 | 414 | 412 | 120 mm² |  | 57 | 7 | 48 | 43 | [86 empty] | Total Load R: 57; Total Load Y: 7; Total Load B: 48; Total Load N: 43 | 57 | 7 | 12.9129 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.380573, 56.875832 | 4716 | Pole (PMT) | 3 | 315 | 04/06/2026, 13:30 | 1 | 237 | 238 | 238 | 414 | 413 | 411 | 185 mm² |  | 89 | 66 | 40 | 52 | [86 empty] | Total Load R: 89; Total Load Y: 66; Total Load B: 40; Total Load N: 52 | 89 | 40 | 20.26 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.381462, 56.867359 | 1101 | Pole (PMT) | 3 | 315 | 04/06/2026, 13:24 | 1 | 237 | 238 | 238 | 411 | 413 | 410 | 120 mm² |  | 86 | 43 | 125 | 46 | 120 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 86; Total Load Y: 43; Total Load B: 125; Total Load N: 46 | 125 | 43 | 28.2489 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.378091, 57.017622 | 1259 | Pole (PMT) |  | 200 | 03/06/2026, 16:16 | 1 | 237 | 237 | 232 | 405 | 405 | 413 | 185 mm² |  | 48 | 22 | 26 | 19 | 50 mm² |  | 4 | 0 | 12 | 10 | [80 empty] | Total Load R: 52; Total Load Y: 22; Total Load B: 38; Total Load N: 29 | 52 | 22 | 18.2385 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.403645, 57.05087 | 2279 | Pole (PMT) |  | 100 | 03/06/2026, 15:58 | 1 | 230 | 227 | 223 | 392 | 388 | 399 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 17 | 14 | [80 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 17; Total Load N: 14 | 17 | 0 | 11.5424 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.401534, 57.049022 | 2203 | Pole (PMT) |  | 100 | 03/06/2026, 15:54 | 1 | 232 | 229 | 224 | 394 | 398 | 399 | 185 mm² |  | 3 | 4 | 2 | 1 | 185 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 3; Total Load Y: 4; Total Load B: 2; Total Load N: 1 | 4 | 2 | 2.7297 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.397223, 57.050161 | 2202 | Pole (PMT) |  | 100 | 03/06/2026, 15:46 | 1 | 231 | 229 | 223 | 392 | 389 | 401 | 185 mm² |  | 15 | 8 | 28 | 23 | [86 empty] | Total Load R: 15; Total Load Y: 8; Total Load B: 28; Total Load N: 23 | 28 | 8 | 19.011 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.393919, 57.044018 | 4270 | Pole (PMT) |  | 50 | 03/06/2026, 15:43 | 1 | 229 | 230 | 228 | 398 | 397 | 401 | 120 mm² |  | 6 | 4 | 5 | 11 | [86 empty] | Total Load R: 6; Total Load Y: 4; Total Load B: 5; Total Load N: 11 | 6 | 4 | 8.2723 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.390012, 57.034183 | 2202 | Pole (PMT) |  | 100 | 03/06/2026, 15:38 | 1 | 227 | 222 | 219 | 387 | 388 | 390 | 120 mm² |  | 8 | 6 | 5 | 12 | [86 empty] | Total Load R: 8; Total Load Y: 6; Total Load B: 5; Total Load N: 12 | 8 | 5 | 5.3624 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.388912, 57.02829 | 1654 | Pole (PMT) |  | 315 | 03/06/2026, 15:31 | 1 | 239 | 234 | 230 | 407 | 397 | 416 | 185 mm² |  | 91 | 141 | 114 | 39 | 120 mm² |  | 18 | 9 | 4 | 13 | [80 empty] | Total Load R: 109; Total Load Y: 150; Total Load B: 118; Total Load N: 52 | 150 | 109 | 33.5688 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.387455, 57.028295 | 1261 | Pole (PMT) |  | 100 | 03/06/2026, 15:23 | 1 | 226 | 223 | 216 | 382 | 378 | 392 | 120 mm² |  | 65 | 40 | 59 | 21 | [86 empty] | Total Load R: 65; Total Load Y: 40; Total Load B: 59; Total Load N: 21 | 65 | 40 | 43.0068 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.387335, 57.023552 | 2328 | Pole (PMT) |  | 315 | 03/06/2026, 15:20 | 1 | 228 | 224 | 219 | 386 | 380 | 395 | 185 mm² |  | 3 | 1 | 8 | 6 | [86 empty] | Total Load R: 3; Total Load Y: 1; Total Load B: 8; Total Load N: 6 | 8 | 1 | 1.698 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.381032, 57.024815 | 1260 | Pole (PMT) |  | 100 | 03/06/2026, 15:14 | 1 | 238 | 235 | 229 | 404 | 398 | 414 | 120 mm² |  | 57 | 15 | 25 | 37 | 120 mm² |  | 18 | 4 | 23 | 15 | [80 empty] | Total Load R: 75; Total Load Y: 19; Total Load B: 48; Total Load N: 52 | 75 | 19 | 52.4811 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.37741, 57.028497 | 1387 | Pole (PMT) |  | 100 | 03/06/2026, 15:06 | 1 | 227 | 222 | 219 | 387 | 378 | 392 | 120 mm² |  | 13 | 6 | 5 | 10 | [86 empty] | Total Load R: 13; Total Load Y: 6; Total Load B: 5; Total Load N: 10 | 13 | 5 | 8.7139 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.378066, 57.022083 | 1735 | Pole (PMT) |  | 315 | 03/06/2026, 15:00 | 1 | 227 | 226 | 217 | 382 | 377 | 396 | 185 mm² |  | 12 | 62 | 74 | 57 | 185 mm² |  | 14 | 20 | 44 | 29 | [80 empty] | Total Load R: 26; Total Load Y: 82; Total Load B: 118; Total Load N: 86 | 118 | 26 | 24.7854 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.382275, 57.016295 | 2211 | Pole (PMT) |  | 315 | 03/06/2026, 14:55 | 1 | 227 | 222 | 218 | 386 | 377 | 394 | 185 mm² |  | 20 | 12 | 17 | 7 | [86 empty] | Total Load R: 20; Total Load Y: 12; Total Load B: 17; Total Load N: 7 | 20 | 12 | 4.2449 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.377192, 57.016344 | 2212 | Pole (PMT) |  | 315 | 03/06/2026, 14:49 | 1 | 227 | 223 | 219 | 394 | 385 | 378 | 185 mm² |  | 18 | 10 | 20 | 4 | [86 empty] | Total Load R: 18; Total Load Y: 10; Total Load B: 20; Total Load N: 4 | 20 | 10 | 4.3329 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.35056, 57.029545 | 1263 | Pole (PMT) |  | 50 | 03/06/2026, 14:42 | 1 | 228 | 230 | 231 | 398 | 396 | 399 | 120 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN4 |  | 1262 | Pole (PMT) |  | 100 | 03/06/2026, 14:31 | 1 | 229 | 228 | 230 | 399 | 398 | 401 | 120 mm² |  | 10 | 9 | 15 | 6 | 120 mm² |  | 11 | 6 | 4 | 9 | [80 empty] | Total Load R: 21; Total Load Y: 15; Total Load B: 19; Total Load N: 15 | 21 | 15 | 14.5129 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.368662, 57.017942 | 4699 | Pole (PMT) |  | 100 | 03/06/2026, 14:17 | 1 | 229 | 227 | 223 | 399 | 388 | 391 | 120 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN4 | 23.381112, 57.011952 | 1258 | Pole (PMT) |  | 315 | 03/06/2026, 13:46 | 1 | 232 | 230 | 227 | 404 | 639 | 392 | 120 mm² |  | 67 | 66 | 121 | 63 | 120 mm² |  | 118 | 107 | 92 | 16 | [80 empty] | Total Load R: 185; Total Load Y: 173; Total Load B: 213; Total Load N: 79 | 213 | 173 | 47.3163 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.380147, 57.006448 | 4376 | Pole (PMT) |  | 100 | 01/06/2026, 16:00 | 1 | 224 | 222 | 218 | 383 | 377 | 388 | 185 mm² |  | 23 | 22 | 18 | 6 | 185 mm² |  | 28 | 14 | 11 | 12 | [80 empty] | Total Load R: 51; Total Load Y: 36; Total Load B: 29; Total Load N: 18 | 51 | 29 | 33.8321 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.382642, 57.005563 | 1991 | Pole (PMT) |  | 100 | 01/06/2026, 15:55 | 1 | 224 | 222 | 217 | 383 | 377 | 388 | 185 mm² |  | 62 | 29 | 47 | 24 | 185 mm² |  | 8 | 10 | 15 | 5 | [80 empty] | Total Load R: 70; Total Load Y: 39; Total Load B: 62; Total Load N: 29 | 70 | 39 | 46.4363 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 |  | 1991 | Pole (PMT) |  | 100 |  | 1 | [98 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN4 | 23.385694, 57.006969 | 1591 | Pole (PMT) |  | 315 | 01/06/2026, 15:49 | 1 | 230 | 225 | 222 | 392 | 385 | 398 | 185 mm² |  | 51 | 22 | 38 | 27 | 185 mm² |  | 15 | 29 | 30 | 10 | [80 empty] | Total Load R: 66; Total Load Y: 51; Total Load B: 68; Total Load N: 37 | 68 | 51 | 14.657 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.387884, 57.005366 | 1257 | Pole (PMT) |  | 315 | 01/06/2026, 15:45 | 1 | 227 | 224 | 221 | 390 | 382 | 393 | 185 mm² |  | 56 | 30 | 60 | 29 | 120 mm² |  | 108 | 80 | 39 | 53 | [80 empty] | Total Load R: 164; Total Load Y: 110; Total Load B: 99; Total Load N: 82 | 164 | 99 | 35.1689 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.388181, 57.006518 | 1256 | Pole (PMT) |  | 100 | 01/06/2026, 15:41 | 1 | 222 | 220 | 214 | 377 | 359 | 382 | 120 mm² |  | 17 | 19 | 26 | 14 | [86 empty] | Total Load R: 17; Total Load Y: 19; Total Load B: 26; Total Load N: 14 | 26 | 17 | 16.9776 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.390154, 57.001091 | 1255 | Pole (PMT) |  | 100 | 01/06/2026, 15:36 | 1 | 224 | 220 | 220 | 383 | 374 | 387 | 120 mm² |  | 23 | 17 | 27 | 11 | 120 mm² |  | 20 | 28 | 6 | 16 | [80 empty] | Total Load R: 43; Total Load Y: 45; Total Load B: 33; Total Load N: 27 | 45 | 33 | 29.8519 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.391328, 57.005297 | 4559 | Pole (PMT) |  | 315 | 01/06/2026, 15:31 | 1 | 226 | 222 | 219 | 385 | 380 | 392 | 185 mm² |  | 63 | 46 | 77 | 19 | [86 empty] | Total Load R: 63; Total Load Y: 46; Total Load B: 77; Total Load N: 19 | 77 | 46 | 16.3005 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.391713, 56.998014 | 1590 | Pole (PMT) |  | 100 | 01/06/2026, 15:26 | 1 | 226 | 221 | 219 | 386 | 378 | 389 | 120 mm² |  | 12 | 9 | 8 | 3 | 185 mm² |  | 26 | 18 | 12 | 6 | [80 empty] | Total Load R: 38; Total Load Y: 27; Total Load B: 20; Total Load N: 9 | 38 | 20 | 25.4057 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.392422, 57.001406 | 1254 | Ground (GMT) |  | 500 | 01/06/2026, 15:20 | 1 | 226 | 223 | 220 | 387 | 380 | 393 | 185 mm² |  | 44 | 56 | 65 | 16 | 185 mm² |  | 138 | 114 | 101 | 25 | 185 mm² |  | 20 | 28 | 44 | 38 | 185 mm² |  | 46 | 24 | 48 | 18 | [68 empty] | Total Load R: 248; Total Load Y: 222; Total Load B: 258; Total Load N: 97 | 258 | 222 | 34.5877 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN4 | 23.395649, 56.994347 | 1252 | Pole (PMT) |  | 315 | 01/06/2026, 15:09 | 1 | 214 | 210 | 207 | 364 | 258 | 370 | 240 mm² |  | 18 | 4 | 35 | 52 | 240 mm² |  | 26 | 39 | 24 | 12 | 120 mm² |  | 118 | 111 | 149 | 28 | [74 empty] | Total Load R: 162; Total Load Y: 154; Total Load B: 208; Total Load N: 92 | 208 | 154 | 41.6308 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.394579, 56.993864 | 1253 | Pole (PMT) |  | 200 | 01/06/2026, 14:58 | 1 | 223 | 220 | 217 | 381 | 374 | 386 | 120 mm² |  | 208 | 179 | 146 | 43 | [86 empty] | Total Load R: 208; Total Load Y: 179; Total Load B: 146; Total Load N: 43 | 208 | 146 | 68.6308 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.395737, 56.993033 | 1149 | Pole (PMT) |  | 100 | 01/06/2026, 14:55 | 1 | 226 | 223 | 219 | 385 | 378 | 393 | 70 mm² |  | 17 | 19 | 18 | 4 | 120 mm² |  | 22 | 19 | 4 | 17 | [80 empty] | Total Load R: 39; Total Load Y: 38; Total Load B: 22; Total Load N: 21 | 39 | 22 | 26.0067 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.403499, 56.993862 | 1146 | Pole (PMT) |  | 100 | 01/06/2026, 14:48 | 1 | 222 | 220 | 218 | 382 | 375 | 383 | 120 mm² |  | 160 | 71 | 53 | 24 | [86 empty] | Total Load R: 160; Total Load Y: 71; Total Load B: 53; Total Load N: 24 | 160 | 53 | 105.8629 | Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.403572, 57.005535 | 4640 | Pole (PMT) |  | 315 | 01/06/2026, 14:41 | 1 | 227 | 224 | 221 | 388 | 382 | 393 | 185 mm² |  | 4 | 14 | 11 | 8 | [86 empty] | Total Load R: 4; Total Load Y: 14; Total Load B: 11; Total Load N: 8 | 14 | 4 | 2.9868 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.402314, 57.001936 | 1147 | Pole (PMT) |  | 315 | 01/06/2026, 14:38 | 1 | 234 | 230 | 227 | 396 | 392 | 406 | 120 mm² |  | 187 | 157 | 210 | 44 | 120 mm² |  | 220 | 235 | 205 | 47 | [80 empty] | Total Load R: 407; Total Load Y: 392; Total Load B: 415; Total Load N: 91 | 415 | 392 | 90.3636 | Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN4 | 23.401773, 56.997044 | 4119 | Pole (PMT) |  | 315 | 01/06/2026, 14:34 | 1 | 229 | 223 | 221 | 388 | 381 | 393 | 185 mm² |  | 125 | 133 | 82 | 57 | [86 empty] | Total Load R: 125; Total Load Y: 133; Total Load B: 82; Total Load N: 57 | 133 | 82 | 28.3748 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.400227, 56.998994 | 2218 | Pole (PMT) |  | 315 | 01/06/2026, 14:28 | 1 | 229 | 228 | 223 | 391 | 389 | 396 | 185 mm² |  | 15 | 12 | 42 | 26 | 185 mm² |  | 16 | 6 | 12 | 15 | [80 empty] | Total Load R: 31; Total Load Y: 18; Total Load B: 54; Total Load N: 41 | 54 | 18 | 11.6097 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.399878, 56.991134 | 1145 | Pole (PMT) |  | 315 | 01/06/2026, 14:20 | 1 | 231 | 229 | 225 | 394 | 390 | 401 | 120 mm² |  | 39 | 67 | 68 | 25 | 120 mm² |  | 92 | 65 | 93 | 22 | [80 empty] | Total Load R: 131; Total Load Y: 132; Total Load B: 161; Total Load N: 47 | 161 | 131 | 34.8797 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.396622, 56.989225 | 1144 | Ground (GMT) |  | 1000 | 01/06/2026, 14:15 | 1 | 223 | 229 | 227 | 387 | 399 | 387 | [6 empty] | 185 mm² |  | 123 | 35 | 50 | 89 | 185 mm² |  | 14 | 16 | 26 | 11 | 185 mm² |  | 134 | 95 | 146 | 11 | 185 mm² |  | 66 | 25 | 86 | 62 | 185 mm² |  | 76 | 48 | 88 | 42 | 185 mm² |  | 69 | 35 | 49 | 16 | [50 empty] | Total Load R: 482; Total Load Y: 254; Total Load B: 445; Total Load N: 231 | 482 | 254 | 32.3086 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.394995, 56.990833 | 1251 | Pole (PMT) |  | 200 | 01/06/2026, 14:09 | 1 | 229 | 229 | 224 | 392 | 390 | 401 | 120 mm² |  | 6 | 10 | 4 | 8 | 120 mm² |  | 82 | 60 | 76 | 52 | [80 empty] | Total Load R: 88; Total Load Y: 70; Total Load B: 80; Total Load N: 60 | 88 | 70 | 29.8744 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.394891, 56.987678 | 4140 | Pole (PMT) |  | 315 | 01/06/2026, 13:58 | 1 | 228 | 229 | 232 | 395 | 399 | 396 | 185 mm² |  | 23 | 118 | 44 | 77 | 185 mm² |  | 45 | 73 | 34 | 38 | [80 empty] | Total Load R: 68; Total Load Y: 191; Total Load B: 78; Total Load N: 115 | 191 | 68 | 41.484 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.395536, 56.9858 | 1443 | Pole (PMT) |  | 315 | 01/06/2026, 13:54 | 1 | 225 | 232 | 230 | 401 | 404 | 398 | 120 mm² |  | 121 | 107 | 123 | 22 | 120 mm² |  | 51 | 14 | 30 | 28 | [80 empty] | Total Load R: 172; Total Load Y: 121; Total Load B: 153; Total Load N: 50 | 172 | 121 | 37.9248 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.396921, 56.984477 | 4523 | Pole (PMT) |  | 100 | 01/06/2026, 13:48 | 1 | 229 | 233 | 233 | 401 | 407 | 399 | 120 mm² |  | 12 | 16 | 6 | 9 | [86 empty] | Total Load R: 12; Total Load Y: 16; Total Load B: 6; Total Load N: 9 | 16 | 6 | 11.1128 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.396946, 56.984506 | 1142 | Pole (PMT) |  | 315 | 01/06/2026, 13:44 | 1 | 229 | 234 | 234 | 401 | 409 | 399 | 120 mm² |  | 118 | 74 | 50 | 48 | 185 mm² |  | 12 | 14 | 6 | 12 | [80 empty] | Total Load R: 130; Total Load Y: 88; Total Load B: 56; Total Load N: 60 | 130 | 56 | 28.6641 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.395406, 56.981246 | 4493 | Pole (PMT) |  | 100 | 01/06/2026, 13:39 | 1 | 221 | 225 | 224 | 384 | 394 | 385 | 120 mm² |  | 6 | 8 | 14 | 10 | [86 empty] | Total Load R: 6; Total Load Y: 8; Total Load B: 14; Total Load N: 10 | 14 | 6 | 9.3115 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.383263, 56.876063 | 1092 | Ground (GMT) |  | 2000 | 28/05/2026, 16:07 | 1 | 238 | 240 | 238 | 413 | 418 | 414 | 120 mm² |  | 64 | 23 | 28 | 37 | 120 mm² |  | 27 | 38 | 63 | 27 | 120 mm² |  | 147 | 75 | 155 | 74 | 120 mm² |  | 34 | 14 | 113 | 87 | 120 mm² |  | 159 | 126 | 124 | 36 | 120 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 96 | 113 | 87 | 15 | [50 empty] | Total Load R: 527; Total Load Y: 389; Total Load B: 570; Total Load N: 276 | 570 | 389 | 20.3871 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.413485, 56.890806 | 1329 | Pole (PMT) |  | 315 | 28/05/2026, 15:49 | 1 | 234 | 235 | 235 | 407 | 407 | 408 | 120 mm² |  | 103 | 63 | 37 | 38 | 185 mm² |  | 38 | 137 | 100 | 60 | [80 empty] | Total Load R: 141; Total Load Y: 200; Total Load B: 137; Total Load N: 98 | 200 | 137 | 44.7584 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.419148, 56.891538 | 4769 | Pole (PMT) |  | 100 | 28/05/2026, 15:44 | 1 | 236 | 238 | 237 | 411 | 412 | 410 | 185 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN2 | 23.412395, 56.889229 | 1919 | Pole (PMT) |  | 315 | 28/05/2026, 15:37 | 1 | 232 | 234 | 234 | 402 | 408 | 405 | 185 mm² |  | 105 | 95 | 90 | 18 | 185 mm² |  | 157 | 137 | 182 | 43 | [80 empty] | Total Load R: 262; Total Load Y: 232; Total Load B: 272; Total Load N: 61 | 272 | 232 | 60.1236 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN2 | 23.409071, 56.889539 | 1098 | Pole (PMT) |  | 315 | 28/05/2026, 15:34 | 1 | 240 | 243 | 242 | 418 | 422 | 417 | 120 mm² |  | 128 | 78 | 116 | 62 | 120 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 128; Total Load Y: 78; Total Load B: 116; Total Load N: 62 | 128 | 78 | 29.4196 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.4044, 56.888872 | 1100 | Ground (GMT) |  | 1000 | 28/05/2026, 15:28 | 1 | 234 | 235 | 234 | 406 | 409 | 407 | [12 empty] | 185 mm² |  | 77 | 55 | 108 | 40 | 185 mm² |  | 72 | 86 | 77 | 35 | 120 mm² |  | 87 | 143 | 132 | 48 | 120 mm² |  | 134 | 128 | 61 | 69 | 120 mm² |  | 73 | 78 | 86 | 26 | 120 mm² |  | 261 | 265 | 311 | 31 | [44 empty] | Total Load R: 704; Total Load Y: 755; Total Load B: 775; Total Load N: 249 | 775 | 704 | 54.499 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN4 | 23.393777, 56.980507 | 1141 | Pole (PMT) |  | 200 | 28/05/2026, 15:26 | 1 | 212 | 222 | 219 | 376 | 368 | 385 | 185 mm² |  | 117 | 57 | 119 | 49 | 120 mm² |  | 36 | 37 | 40 | 14 | [80 empty] | Total Load R: 153; Total Load Y: 94; Total Load B: 159; Total Load N: 63 | 159 | 94 | 51.7745 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.402199, 56.88743 | 1099 | Pole (PMT) |  | 315 | 28/05/2026, 15:21 | 1 | 236 | 238 | 238 | 413 | 413 | 410 | 185 mm² |  | 141 | 37 | 42 | 89 | [86 empty] | Total Load R: 141; Total Load Y: 37; Total Load B: 42; Total Load N: 89 | 141 | 37 | 32.0198 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.392796, 56.980202 | 2300 | Pole (PMT) |  | 315 | 28/05/2026, 15:21 | 1 | 204 | 213 | 210 | 360 | 355 | 371 | 120 mm² |  | 13 | 17 | 20 | 11 | 185 mm² |  | 24 | 15 | 16 | 10 | [80 empty] | Total Load R: 37; Total Load Y: 32; Total Load B: 36; Total Load N: 21 | 37 | 32 | 7.3241 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN2 | 23.398078, 56.887383 | 1097 | Pole (PMT) |  | 100 | 28/05/2026, 15:16 | 1 | 235 | 234 | 238 | 410 | 415 | 408 | 70 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN4 | 23.393501, 56.974592 | 1140 | Pole (PMT) |  | 315 | 28/05/2026, 15:16 | 1 | 214 | 223 | 220 | 377 | 373 | 386 | 120 mm² |  | 179 | 160 | 158 | 40 | 185 mm² |  | 55 | 65 | 40 | 23 | [80 empty] | Total Load R: 234; Total Load Y: 225; Total Load B: 198; Total Load N: 63 | 234 | 198 | 48.5073 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN2 | 23.395883, 56.889131 | 1096 | Pole (PMT) |  | 315 | 28/05/2026, 15:10 | 1 | 242 | 247 | 247 | 425 | 428 | 423 | 120 mm² |  | 175 | 121 | 107 | 45 | 120 mm² |  | 40 | 21 | 29 | 16 | [80 empty] | Total Load R: 215; Total Load Y: 142; Total Load B: 136; Total Load N: 61 | 215 | 136 | 50.2432 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.370364, 56.923903 | 4721 | Pole (PMT) |  | 100 | 28/05/2026, 15:06 | 1 | 215 | 223 | 222 | 372 | 375 | 391 | 120 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN4 | 23.353282, 56.909336 | 1125 | Pole (PMT) |  | 100 | 28/05/2026, 15:01 | 1 | 215 | 220 | 216 | 416 | 414 | 415 | 120 mm² |  | 6 | 8 | 0 | 10 | [86 empty] | Total Load R: 6; Total Load Y: 8; Total Load B: 0; Total Load N: 10 | 8 | 0 | 5.7643 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.401953, 56.892245 | 2312 | Pole (PMT) |  | 315 | 28/05/2026, 15:01 | 1 | 233 | 235 | 235 | 406 | 408 | 409 | 185 mm² |  | 13 | 17 | 10 | 8 | 185 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 13; Total Load Y: 17; Total Load B: 10; Total Load N: 8 | 17 | 10 | 3.7951 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.413236, 56.972744 | 1139 | Pole (PMT) |  | 100 | 28/05/2026, 14:58 | 1 | 213 | 222 | 219 | 376 | 368 | 387 | 120 mm² |  | 36 | 85 | 54 | 25 | [86 empty] | Total Load R: 36; Total Load Y: 85; Total Load B: 54; Total Load N: 25 | 85 | 36 | 55.3563 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.408379, 56.971662 | 4392 | Pole (PMT) |  | 100 | 28/05/2026, 14:55 | 1 | 214 | 222 | 224 | 376 | 374 | 388 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 15 | 6 | 8 | 10 | [80 empty] | Total Load R: 15; Total Load Y: 6; Total Load B: 8; Total Load N: 10 | 15 | 6 | 9.7688 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.392379, 56.885686 | 4359 | Pole (PMT) |  | 100 | 28/05/2026, 15:05 | 1 | 238 | 235 | 237 | 410 | 408 | 411 | 120 mm² |  | 3 | 8 | 8 | 7 | [86 empty] | Total Load R: 3; Total Load Y: 8; Total Load B: 8; Total Load N: 7 | 8 | 3 | 5.6811 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.40095, 56.968362 | 4605 | Pole (PMT) |  | 100 | 28/05/2026, 14:53 | 1 | 215 | 223 | 222 | 372 | 375 | 391 | 185 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN2 | 23.390083, 56.884282 | 4142 | Pole (PMT) |  | 315 | 28/05/2026, 14:46 | 1 | 236 | 237 | 238 | 411 | 413 | 411 | 185 mm² |  | 5 | 3 | 16 | 14 | [86 empty] | Total Load R: 5; Total Load Y: 3; Total Load B: 16; Total Load N: 14 | 16 | 3 | 3.6159 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.397374, 56.97105 | 1138 | Pole (PMT) |  | 100 | 28/05/2026, 14:45 | 1 | 299 | 209 | 209 | 349 | 352 | 366 | 120 mm² |  | 153 | 106 | 89 | 47 | [86 empty] | Total Load R: 153; Total Load Y: 106; Total Load B: 89; Total Load N: 47 | 153 | 89 | 92.4863 | Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.395039, 56.965196 | 1137 | Pole (PMT) |  | 100 | 28/05/2026, 14:40 | 1 | 217 | 226 | 224 | 380 | 379 | 394 | 120 mm² |  | 77 | 50 | 88 | 37 | 185 mm² |  | 15 | 27 | 6 | 11 | [80 empty] | Total Load R: 92; Total Load Y: 77; Total Load B: 94; Total Load N: 48 | 94 | 77 | 61.8689 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN2 | 23.3848, 56.881396 | 1095 | Ground (GMT) |  | 1000 | 28/05/2026, 14:41 | 1 | 236 | 238 | 238 | 416 | 415 | 408 | 185 mm² |  | 7 | 28 | 14 | 20 | 185 mm² |  | 134 | 65 | 127 | 89 | 185 mm² |  | 54 | 66 | 47 | 13 | 185 mm² |  | 168 | 116 | 148 | 49 | [68 empty] | Total Load R: 363; Total Load Y: 275; Total Load B: 336; Total Load N: 171 | 363 | 275 | 26.1554 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.39025, 56.96482 | 1136 | Pole (PMT) |  | 100 | 28/05/2026, 14:36 | 1 | 214 | 222 | 222 | 375 | 374 | 390 | 120 mm² |  | 35 | 45 | 40 | 13 | 120 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 35; Total Load Y: 45; Total Load B: 40; Total Load N: 13 | 45 | 35 | 29.2284 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.384935, 56.878662 | 1091 | Ground (GMT) |  | 1000 | 28/05/2026, 14:34 | 1 | 234 | 236 | 237 | 409 | 412 | 406 | [24 empty] | 185 mm² |  | 58 | 54 | 47 | 35 | 185 mm² |  | 126 | 85 | 26 | 84 | 185 mm² |  | 164 | 146 | 158 | 36 | [50 empty] | Total Load R: 348; Total Load Y: 285; Total Load B: 231; Total Load N: 155 | 348 | 231 | 24.6526 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.385303, 56.960748 | 2361 | Pole (PMT) |  | 315 | 28/05/2026, 14:31 | 1 | 198 | 204 | 206 | 345 | 349 | 358 | 185 mm² |  | 92 | 42 | 89 | 47 | 185 mm² |  | 224 | 108 | 44 | 84 | [80 empty] | Total Load R: 316; Total Load Y: 150; Total Load B: 133; Total Load N: 131 | 316 | 133 | 59.9455 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.38693, 56.878828 | 1089 | Ground (GMT) |  | 1000 | 28/05/2026, 14:27 | 1 | 236 | 237 | 238 | 413 | 414 | 419 | 120 mm² |  | 122 | 64 | 87 | 62 | 120 mm² |  | 211 | 157 | 170 | 43 | [80 empty] | Total Load R: 333; Total Load Y: 221; Total Load B: 257; Total Load N: 105 | 333 | 221 | 23.8207 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.386647, 56.961419 | 1135 | Pole (PMT) |  | 100 | 28/05/2026, 14:25 | 1 | 199 | 205 | 206 | 349 | 358 | 350 | 120 mm² |  | 32 | 57 | 18 | 30 | [86 empty] | Total Load R: 32; Total Load Y: 57; Total Load B: 18; Total Load N: 30 | 57 | 18 | 34.4557 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.387428, 56.958719 | 1924 | Pole (PMT) |  | 100 | 28/05/2026, 14:20 | 1 | 201 | 208 | 208 | 351 | 354 | 365 | 120 mm² |  | 13 | 6 | 12 | 4 | 185 mm² |  | 30 | 20 | 12 | 11 | [80 empty] | Total Load R: 43; Total Load Y: 26; Total Load B: 24; Total Load N: 15 | 43 | 24 | 26.1418 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.376581, 56.965205 | 1134 | Pole (PMT) |  | 100 | 28/05/2026, 14:15 | 1 | 201 | 210 | 209 | 352 | 354 | 368 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 52 | 6 | 33 | 41 | [80 empty] | Total Load R: 52; Total Load Y: 6; Total Load B: 33; Total Load N: 41 | 52 | 6 | 31.7035 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.377465, 56.96096 | 475 | Pole (PMT) |  | 315 | 28/05/2026, 14:10 | 1 | 204 | 210 | 210 | 356 | 358 | 368 | 185 mm² |  | 83 | 38 | 17 | 45 | 185 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 83; Total Load Y: 38; Total Load B: 17; Total Load N: 45 | 83 | 17 | 16.2472 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.386566, 56.874768 | 1087 | Ground (GMT) |  | 1000 | 28/05/2026, 14:16 | 1 | 236 | 237 | 238 | 413 | 415 | 410 | 185 mm² |  | 38 | 28 | 82 | 52 | 185 mm² |  | 67 | 80 | 68 | 27 | 185 mm² |  | 36 | 52 | 33 | 10 | 185 mm² |  | 81 | 105 | 54 | 67 | 185 mm² |  | 116 | 68 | 81 | 40 | 185 mm² |  | 122 | 193 | 127 | 50 | 185 mm² |  | 106 | 81 | 84 | 25 | [50 empty] | Total Load R: 566; Total Load Y: 607; Total Load B: 529; Total Load N: 271 | 607 | 529 | 43.421 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN4 | 23.380055, 56.95979 | 1133 | Pole (PMT) |  | 315 | 28/05/2026, 14:05 | 1 | 205 | 211 | 211 | 356 | 359 | 370 | 120 mm² | [5 empty] | 120 mm² |  | 143 | 34 | 121 | 100 | [80 empty] | Total Load R: 143; Total Load Y: 34; Total Load B: 121; Total Load N: 100 | 143 | 34 | 27.9921 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.384461, 56.874191 | 1090 | Pole (PMT) |  | 315 | 28/05/2026, 14:03 | 1 | 238 | 236 | 238 | 416 | 413 | 408 | 120 mm² |  | 43 | 105 | 91 | 65 | 120 mm² |  | 78 | 108 | 78 | 23 | [80 empty] | Total Load R: 121; Total Load Y: 213; Total Load B: 169; Total Load N: 88 | 213 | 121 | 48.7218 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.382152, 56.959538 | 1132 | Pole (PMT) |  | 315 | 28/05/2026, 13:58 | 1 | 214 | 220 | 221 | 372 | 375 | 385 | 120 mm² |  | 36 | 19 | 42 | 21 | 185 mm² |  | 98 | 40 | 38 | 59 | [80 empty] | Total Load R: 134; Total Load Y: 59; Total Load B: 80; Total Load N: 80 | 134 | 59 | 27.4093 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.384648, 56.956893 | 1131 | Pole (PMT) |  | 315 | 28/05/2026, 13:54 | 1 | 216 | 221 | 222 | 371 | 378 | 387 | 120 mm² |  | 43 | 20 | 29 | 21 | 70 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 43; Total Load Y: 20; Total Load B: 29; Total Load N: 21 | 43 | 20 | 8.7719 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.386252, 56.956143 | 2075 | Pole (PMT) |  | 200 | 28/05/2026, 13:46 | 1 | 204 | 210 | 212 | 355 | 360 | 368 | 120 mm² |  | 5 | 11 | 6 | 10 | 185 mm² |  | 48 | 15 | 8 | 42 | [80 empty] | Total Load R: 53; Total Load Y: 26; Total Load B: 14; Total Load N: 52 | 53 | 14 | 16.2943 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.382047, 56.94618 | 1671 | Pole (PMT) |  | 100 | 28/05/2026, 13:41 | 1 | 208 | 213 | 213 | 364 | 372 | 372 | 240 mm² |  | 27 | 13 | 37 | 23 | [86 empty] | Total Load R: 27; Total Load Y: 13; Total Load B: 37; Total Load N: 23 | 37 | 13 | 23.3273 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.342247, 56.982935 | 1130 | Pole (PMT) |  | 100 | 28/05/2026, 13:27 | 1 | 215 | 216 | 217 | 372 | 373 | 377 | 120 mm² |  | 37 | 52 | 62 | 12 | [86 empty] | Total Load R: 37; Total Load Y: 52; Total Load B: 62; Total Load N: 12 | 62 | 37 | 39.948 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.337487, 56.981002 | 1129 | Pole (PMT) |  | 50 | 28/05/2026, 13:23 | 1 | 213 | 216 | 218 | 370 | 373 | 378 | 70 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 24 | 9 | 12 | 12 | [80 empty] | Total Load R: 24; Total Load Y: 9; Total Load B: 12; Total Load N: 12 | 24 | 9 | 30.7612 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.338262, 56.977068 | 1693 | Pole (PMT) |  | 100 | 28/05/2026, 13:18 | 1 | 216 | 218 | 219 | 375 | 377 | 381 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 8 | 12 | 6 | 4 | [80 empty] | Total Load R: 8; Total Load Y: 12; Total Load B: 6; Total Load N: 4 | 12 | 6 | 7.7942 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.383056, 56.871634 | 1094 | Ground (GMT) |  | 1000 | 28/05/2026, 13:09 | 1 | 237 | 240 | 241 | 416 | 418 | 412 | 120 mm² |  | 112 | 31 | 68 | 65 | [12 empty] | 120 mm² |  | 72 | 46 | 64 | 37 | 120 mm² |  | 160 | 69 | 40 | 90 | 120 mm² |  | 27 | 34 | 12 | 17 | 185 mm² |  | 71 | 85 | 120 | 42 | 185 mm² |  | 50 | 61 | 30 | 33 | [44 empty] | Total Load R: 492; Total Load Y: 326; Total Load B: 334; Total Load N: 284 | 492 | 326 | 35.4502 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.363613, 56.95607 | 1128 | Pole (PMT) |  | 100 | 28/05/2026, 13:09 | 1 | 227 | 232 | 233 | 394 | 399 | 406 | 185 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 38 | 0 | 22 | 29 | [80 empty] | Total Load R: 38; Total Load Y: 0; Total Load B: 22; Total Load N: 29 | 38 | 0 | 25.9323 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.387349, 56.873424 | 1088 | Pole (PMT) |  | 100 | 28/05/2026, 12:54 | 1 | 238 | 238 | 240 | 415 | 417 | 413 | 70 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN4 | 23.372968, 56.953842 | 1127 | Ground (GMT) |  | 1000 | 28/05/2026, 12:52 | 1 | 229 | 230 | 232 | 397 | 400 | 402 | 185 mm² |  | 29 | 25 | 32 | 6 | 185 mm² |  | 26 | 55 | 38 | 25 | 185 mm² |  | 60 | 18 | 26 | 43 | 185 mm² |  | 38 | 22 | 11 | 27 | 185 mm² |  | 128 | 103 | 59 | 34 | [62 empty] | Total Load R: 281; Total Load Y: 223; Total Load B: 166; Total Load N: 135 | 281 | 166 | 19.3222 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.386684, 56.86412 | 1086 | Pole (PMT) |  | 200 | 28/05/2026, 12:47 | 1 | 238 | 238 | 240 | 415 | 417 | 413 | 185 mm² |  | 50 | 85 | 62 | 35 | 185 mm² |  | 68 | 65 | 54 | 22 | [80 empty] | Total Load R: 118; Total Load Y: 150; Total Load B: 116; Total Load N: 57 | 150 | 116 | 53.9101 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 |  | 1126 | Pole (PMT) |  | 100 | 28/05/2026, 12:46 | 1 | 229 | 231 | 232 | 398 | 398 | 400 | 185 mm² |  | 0 | 23 | 23 | 16 | 185 mm² |  | 17 | 8 | 6 | 10 | [80 empty] | Total Load R: 17; Total Load Y: 31; Total Load B: 29; Total Load N: 26 | 31 | 17 | 21.37 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.387958, 56.86285 | 2271 | Pole (PMT) |  | 50 | 28/05/2026, 12:39 | 1 | 242 | 241 | 244 | 424 | 422 | 420 | 70 mm² |  | 0 | 4 | 0 | 4 | [86 empty] | Total Load R: 0; Total Load Y: 4; Total Load B: 0; Total Load N: 4 | 4 | 0 | 5.8751 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.373144, 56.909418 | 1124 | Pole (PMT) |  | 315 | 28/05/2026, 12:28 | 1 | 229 | 230 | 231 | 397 | 400 | 401 | 185 mm² |  | 24 | 6 | 4 | 24 | 185 mm² |  | 12 | 25 | 8 | 20 | [80 empty] | Total Load R: 36; Total Load Y: 31; Total Load B: 12; Total Load N: 44 | 36 | 12 | 7.8586 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.387667, 56.838284 | 2272 | Pole (PMT) |  | 315 | 28/05/2026, 12:14 | 1 | 242 | 242 | 244 | 418 | 423 | 421 | 185 mm² |  | 5 | 6 | 8 | 6 | 185 mm² |  | 18 | 6 | 8 | 11 | [80 empty] | Total Load R: 23; Total Load Y: 12; Total Load B: 16; Total Load N: 17 | 23 | 12 | 5.2863 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.386882, 56.842673 | 1288 | Ground (GMT) |  | 1000 | 26/05/2026, 15:08 | 1 | 238 | 233 | 235 | 406 | 405 | 402 | 185 mm² |  | 45 | 41 | 42 | 13 | 185 mm² |  | 78 | 50 | 60 | 30 | 185 mm² |  | 200 | 100 | 130 | 90 | [74 empty] | Total Load R: 323; Total Load Y: 191; Total Load B: 232; Total Load N: 133 | 323 | 191 | 22.7138 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.386827, 56.849151 | 1287 | Ground (GMT) |  | 1000 | 26/05/2026, 14:52 | 1 | 244 | 243 | 244 | 426 | 427 | 426 | [12 empty] | 185 mm² |  | 24 | 15 | 35 | 13 | 185 mm² |  | 140 | 170 | 160 | 30 | 185 mm² |  | 120 | 20 | 53 | 73 | [62 empty] | Total Load R: 284; Total Load Y: 205; Total Load B: 248; Total Load N: 116 | 284 | 205 | 20.955 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.387491, 56.848962 | 1917 | Ground (GMT) |  | 1000 | 26/05/2026, 14:43 | 1 | 245 | 245 | 243 | 426 | 425 | 426 | 185 mm² |  | 90 | 120 | 100 | 20 | 185 mm² |  | 220 | 230 | 190 | 110 | [80 empty] | Total Load R: 310; Total Load Y: 350; Total Load B: 290; Total Load N: 130 | 350 | 290 | 25.8249 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.386565, 56.851428 | 1281 | Ground (GMT) |  | 1000 | 26/05/2026, 14:34 | 1 | 243 | 244 | 243 | 425 | 425 | 423 | 120 mm² |  | 22 | 11 | 27 | 15 | 185 mm² |  | 16 | 40 | 20 | 15 | 185 mm² |  | 190 | 120 | 140 | 26 | 120 mm² |  | 71 | 41 | 34 | 33 | 120 mm² |  | 10 | 11 | 12 | 3 | 185 mm² |  | 4 | 2 | 0 | 0 | 185 mm² |  | 180 | 70 | 125 | 70 | 185 mm² |  | 75 | 92 | 105 | 90 | [44 empty] | Total Load R: 568; Total Load Y: 387; Total Load B: 463; Total Load N: 252 | 568 | 387 | 41.8117 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.389867, 56.851509 | 1452 | Ground (GMT) |  | 1000 | 26/05/2026, 14:22 | 1 | 244 | 244 | 242 | 425 | 425 | 421 | [36 empty] | 120 mm² |  | 65 | 40 | 65 | 20 | 185 mm² |  | 160 | 130 | 150 | 22 | [44 empty] | Total Load R: 225; Total Load Y: 170; Total Load B: 215; Total Load N: 42 | 225 | 170 | 16.5627 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.393636, 56.856169 | 1286 | Pole (PMT) |  | 100 | 26/05/2026, 14:16 | 1 | 240 | 240 | 241 | 420 | 418 | 420 | 120 mm² |  | 38 | 52 | 32 | 12 | 120 mm² |  | 10 | 6 | 14 | 8 | [80 empty] | Total Load R: 48; Total Load Y: 58; Total Load B: 46; Total Load N: 20 | 58 | 46 | 42.1928 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.393636, 56.856169 | 1285 | Pole (PMT) |  | 100 | 26/05/2026, 14:14 | 1 | 241 | 240 | 242 | 420 | 424 | 421 | 120 mm² |  | 18 | 12 | 20 | 8 | [86 empty] | Total Load R: 18; Total Load Y: 12; Total Load B: 20; Total Load N: 8 | 20 | 12 | 14.5492 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.393636, 56.856169 | 1284 | Pole (PMT) |  | 100 | 26/05/2026, 14:13 | 1 | 242 | 241 | 242 | 424 | 424 | 424 | 120 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN5 | 23.399086, 56.852089 | 1283 | Pole (PMT) |  | 315 | 26/05/2026, 13:54 | 1 | 243 | 243 | 241 | 423 | 421 | 423 | [6 empty] | 120 mm² |  | 120 | 90 | 150 | 30 | [80 empty] | Total Load R: 120; Total Load Y: 90; Total Load B: 150; Total Load N: 30 | 150 | 90 | 34.8885 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.389423, 56.85479 | 1475 | Ground (GMT) |  | 1000 | 26/05/2026, 13:50 | 1 | 247 | 246 | 247 | 428 | 430 | 427 | [24 empty] | 120 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 116 | 148 | 139 | 30 | 185 mm² |  | 14 | 8 | 7 | 11 | 185 mm² |  | 85 | 90 | 120 | 35 | [44 empty] | Total Load R: 215; Total Load Y: 246; Total Load B: 266; Total Load N: 76 | 266 | 215 | 19.7191 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN5 | 23.385159, 56.854351 | 1463 | Pole (PMT) |  | 100 | 26/05/2026, 13:43 | 1 | 238 | 240 | 238 | 418 | 416 | 416 | [6 empty] | 120 mm² |  | 50 | 70 | 40 | 30 | [80 empty] | Total Load R: 50; Total Load Y: 70; Total Load B: 40; Total Load N: 30 | 70 | 40 | 50.6798 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.385159, 56.854351 | 2295 | Ground (GMT) |  | 1000 | 26/05/2026, 13:38 | 1 | 242 | 243 | 242 | 420 | 420 | 421 | 120 mm² |  | 50 | 20 | 17 | 30 | 120 mm² |  | 70 | 70 | 115 | 22 | 185 mm² |  | 0 | 0 | 0 | 0 | [74 empty] | Total Load R: 120; Total Load Y: 90; Total Load B: 132; Total Load N: 52 | 132 | 90 | 9.6025 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN6 | 23.385147, 56.854391 | 1280 | Pole (PMT) |  | 315 | 26/05/2026, 13:34 | 1 | 230 | 231 | 230 | 400 | 400 | 401 | 185 mm² |  | 108 | 53 | 76 | 26 | 120 mm² |  | 40 | 35 | 30 | 8 | [80 empty] | Total Load R: 148; Total Load Y: 88; Total Load B: 106; Total Load N: 34 | 148 | 88 | 32.5516 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN6 | 23.384682, 56.851435 | 1278 | Pole (PMT) |  | 315 | 26/05/2026, 13:30 | 1 | 245 | 242 | 243 | 421 | 422 | 420 | 120 mm² |  | 80 | 100 | 70 | 20 | 185 mm² |  | 30 | 40 | 20 | 8 | [80 empty] | Total Load R: 110; Total Load Y: 140; Total Load B: 90; Total Load N: 28 | 140 | 90 | 32.4086 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN6 | 23.382156, 56.847319 | 1274 | Ground (GMT) |  | 1000 | 26/05/2026, 13:26 | 1 | 232 | 232 | 231 | 410 | 408 | 410 | [6 empty] | 185 mm² |  | 13 | 20 | 15 | 18 | 185 mm² |  | 40 | 50 | 60 | 15 | 185 mm² |  | 90 | 70 | 90 | 25 | 185 mm² |  | 140 | 90 | 80 | 40 | 185 mm² |  | 50 | 60 | 70 | 30 | [56 empty] | Total Load R: 333; Total Load Y: 290; Total Load B: 315; Total Load N: 128 | 333 | 290 | 23.6477 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN6 | 23.383357, 56.843152 | 1276 | Pole (PMT) |  | 100 | 26/05/2026, 13:19 | 1 | 236 | 235 | 236 | 413 | 415 | 413 | 70 mm² |  | 23 | 23 | 23 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 23; Total Load Y: 23; Total Load B: 23; Total Load N: 0 | 23 | 23 | 16.4528 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN6 | 23.383155, 56.843905 | 1275 | Ground (GMT) |  | 1000 | 26/05/2026, 13:14 | 1 | 242 | 242 | 240 | 421 | 421 | 420 | [18 empty] | 185 mm² |  | 60 | 50 | 50 | 18 | 185 mm² |  | 70 | 60 | 40 | 30 | 185 mm² |  | 90 | 70 | 115 | 70 | 185 mm² |  | 70 | 40 | 90 | 30 | 185 mm² |  | 247 | 211 | 384 | 121 | [44 empty] | Total Load R: 537; Total Load Y: 431; Total Load B: 679; Total Load N: 269 | 679 | 431 | 49.5122 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN6 | 23.388522, 56.834249 | 1364 | Ground (GMT) |  | 1000 | 26/05/2026, 12:45 | 1 | 240 | 252 | 252 | 447 | 445 | 447 | [36 empty] | 185 mm² |  | 111 | 130 | 120 | 19 | 185 mm² |  | 90 | 40 | 60 | 35 | [44 empty] | Total Load R: 201; Total Load Y: 170; Total Load B: 180; Total Load N: 54 | 201 | 170 | 15.562 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN6 | 23.384343, 56.8389 | 1409 | Ground (GMT) |  | 1000 | 26/05/2026, 12:38 | 1 | 244 | 245 | 243 | 425 | 426 | 424 | [12 empty] | 185 mm² |  | 55 | 33 | 27 | 23 | 185 mm² |  | 80 | 70 | 90 | 12 | 185 mm² |  | 112 | 70 | 126 | 46 | 185 mm² |  | 40 | 35 | 40 | 12 | 185 mm² |  | 6 | 8 | 2 | 2 | 185 mm² |  | 60 | 40 | 50 | 11 | [44 empty] | Total Load R: 353; Total Load Y: 256; Total Load B: 335; Total Load N: 106 | 353 | 256 | 25.9851 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN6 | 23.3807, 56.838122 | 4606 | Pole (PMT) |  | 100 | 26/05/2026, 12:30 | 1 | 246 | 246 | 245 | 425 | 425 | 424 | 185 mm² |  | 4 | 0 | 2 | 1 | [86 empty] | Total Load R: 4; Total Load Y: 0; Total Load B: 2; Total Load N: 1 | 4 | 0 | 2.9445 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN6 | 23.393279, 56.717482 | 4512 | Pole (PMT) |  | 100 | 26/05/2026, 12:24 | 1 | 245 | 246 | 245 | 425 | 424 | 425 | 185 mm² |  | 4 | 6 | 4 | 3 | 185 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 4; Total Load Y: 6; Total Load B: 4; Total Load N: 3 | 6 | 4 | 4.4167 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN6 | 23.393279, 56.717482 | 4391 | Pole (PMT) |  | 100 | 26/05/2026, 12:21 | 1 | 246 | 246 | 245 | 426 | 125 | 426 | 185 mm² |  | 8 | 12 | 10 | 6 | 185 mm² |  | 10 | 8 | 5 | 3 | [80 empty] | Total Load R: 18; Total Load Y: 20; Total Load B: 15; Total Load N: 9 | 20 | 15 | 14.7571 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN6 | 23.393279, 56.717482 | 4350 | Pole (PMT) |  | 100 | 26/05/2026, 12:15 | 1 | 243 | 244 | 246 | 426 | 424 | 427 | 185 mm² |  | 50 | 31 | 31 | 8 | 185 mm² |  | 11 | 0 | 8 | 9 | [80 empty] | Total Load R: 61; Total Load Y: 31; Total Load B: 39; Total Load N: 17 | 61 | 31 | 45.0091 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.39375, 56.813382 | 2275 | Pole (PMT) |  | 315 | 21/05/2026, 15:46 | 1 | 241 | 240 | 240 | 417 | 415 | 416 | 185 mm² |  | 5 | 23 | 6 | 15 | [86 empty] | Total Load R: 5; Total Load Y: 23; Total Load B: 6; Total Load N: 15 | 23 | 5 | 5.2737 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.396848, 56.836497 | 1772 | Ground (GMT) |  | 1000 | 21/05/2026, 15:31 | 1 | 240 | 240 | 241 | 417 | 418 | 416 | [12 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 5 | 21 | 6 | 16 | 185 mm² |  | 12 | 9 | 9 | 4 | 185 mm² |  | 20 | 18 | 30 | 7 | 185 mm² |  | 15 | 10 | 25 | 14 | 185 mm² |  | 2 | 0 | 0 | 9 | [44 empty] | Total Load R: 54; Total Load Y: 58; Total Load B: 70; Total Load N: 50 | 70 | 54 | 5.0559 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.399308, 56.835504 | 1952 | Ground (GMT) |  | 500 | 21/05/2026, 15:18 | 1 | 240 | 241 | 241 | 417 | 417 | 417 | [12 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 21 | 10 | 13 | 9 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | [56 empty] | Total Load R: 21; Total Load Y: 10; Total Load B: 13; Total Load N: 9 | 21 | 10 | 3.0335 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.39299, 56.828558 | 2008 | Pole (PMT) |  | 315 | 21/05/2026, 15:06 | 1 | 241 | 241 | 241 | 418 | 418 | 417 | 185 mm² |  | 7 | 14 | 15 | 7 | 185 mm² |  | 5 | 4 | 41 | 30 | [80 empty] | Total Load R: 12; Total Load Y: 18; Total Load B: 56; Total Load N: 37 | 56 | 12 | 12.8711 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.39299, 56.828558 | 2137 | Ground (GMT) |  | 500 | 21/05/2026, 14:57 | 1 | 241 | 242 | 243 | 419 | 421 | 417 | [18 empty] | 240 mm² |  | 30 | 23 | 28 | 4 | 185 mm² |  | 0 | 0 | 8 | 6 | 185 mm² |  | 0 | 0 | 0 | 0 | [56 empty] | Total Load R: 30; Total Load Y: 23; Total Load B: 36; Total Load N: 10 | 36 | 23 | 5.2253 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.39299, 56.828558 | 2226 | Pole (PMT) |  | 315 | 21/05/2026, 14:47 | 1 | 240 | 241 | 240 | 417 | 417 | 418 | 185 mm² |  | 11 | 9 | 20 | 7 | 185 mm² |  | 63 | 22 | 32 | 26 | [80 empty] | Total Load R: 74; Total Load Y: 31; Total Load B: 52; Total Load N: 33 | 74 | 31 | 16.9675 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.39299, 56.828558 | 2182 | Ground (GMT) |  | 1000 | 21/05/2026, 14:41 | 1 | 241 | 242 | 242 | 419 | 419 | 417 | [36 empty] | 240 mm² |  | 2 | 0 | 9 | 5 | 185 mm² |  | 34 | 18 | 23 | 8 | [44 empty] | Total Load R: 36; Total Load Y: 18; Total Load B: 32; Total Load N: 13 | 36 | 18 | 2.6126 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.399304, 56.819298 | 2109 | Pole (PMT) |  | 315 | 21/05/2026, 14:33 | 1 | 241 | 241 | 242 | 420 | 418 | 418 | 185 mm² |  | 62 | 58 | 35 | 22 | 185 mm² |  | 20 | 23 | 10 | 23 | [80 empty] | Total Load R: 82; Total Load Y: 81; Total Load B: 45; Total Load N: 45 | 82 | 45 | 18.9371 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.399304, 56.819298 | 2012 | Ground (GMT) |  | 1000 | 21/05/2026, 14:24 | 1 | 243 | 242 | 243 | 420 | 420 | 421 | 185 mm² |  | 8 | 31 | 42 | 24 | 185 mm² |  | 32 | 21 | 33 | 11 | 185 mm² |  | 3 | 8 | 19 | 11 | 185 mm² |  | 52 | 39 | 30 | 15 | [68 empty] | Total Load R: 95; Total Load Y: 99; Total Load B: 124; Total Load N: 61 | 124 | 95 | 9.0205 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.399315, 56.819307 | 2181 | Ground (GMT) |  | 1000 | 21/05/2026, 14:15 | 1 | 241 | 242 | 242 | 420 | 421 | 420 | [24 empty] | 185 mm² |  | 24 | 17 | 30 | 6 | 185 mm² |  | 20 | 10 | 8 | 9 | 185 mm² |  | 14 | 8 | 9 | 7 | 185 mm² |  | 10 | 5 | 3 | 6 | [44 empty] | Total Load R: 68; Total Load Y: 40; Total Load B: 50; Total Load N: 28 | 68 | 40 | 4.9467 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.414432, 56.821717 | 4347 | Pole (PMT) |  | 100 | 21/05/2026, 14:04 | 1 | 243 | 243 | 244 | 424 | 422 | 422 | 185 mm² |  | 11 | 0 | 2 | 10 | [86 empty] | Total Load R: 11; Total Load Y: 0; Total Load B: 2; Total Load N: 10 | 11 | 0 | 8.0783 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.415584, 56.812301 | 1298 | Pole (PMT) |  | 100 | 21/05/2026, 13:58 | 1 | 240 | 244 | 242 | 417 | 422 | 417 | 120 mm² |  | 57 | 22 | 36 | 28 | [86 empty] | Total Load R: 57; Total Load Y: 22; Total Load B: 36; Total Load N: 28 | 57 | 22 | 41.1691 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.426131, 56.828301 | 1299 | Pole (PMT) |  | 200 | 21/05/2026, 13:51 | 1 | 238 | 240 | 238 | 411 | 415 | 412 | 120 mm² |  | 32 | 11 | 51 | 35 | 120 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 32; Total Load Y: 11; Total Load B: 51; Total Load N: 35 | 51 | 11 | 18.1528 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.426131, 56.828301 | 1300 | Pole (PMT) |  | 315 | 21/05/2026, 13:42 | 1 | 245 | 246 | 247 | 425 | 427 | 424 |  |  | 70 | 130 | 60 | 56 | 185 mm² |  | 82 | 45 | 20 | 47 | [80 empty] | Total Load R: 152; Total Load Y: 175; Total Load B: 80; Total Load N: 103 | 175 | 80 | 40.8956 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.426131, 56.828301 | 4383 | Pole (PMT) |  | 100 | 21/05/2026, 13:31 | 1 | 242 | 244 | 243 | 420 | 423 | 420 | 185 mm² |  | 4 | 3 | 5 | 4 | [86 empty] | Total Load R: 4; Total Load Y: 3; Total Load B: 5; Total Load N: 4 | 5 | 3 | 3.6373 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN5 | 23.426216, 56.82685 | 1383 | Pole (PMT) |  | 100 | 21/05/2026, 13:16 | 1 | 244 | 246 | 244 | 422 | 425 | 423 | 120 mm² |  | 45 | 20 | 40 | 30 | 185 mm² |  | 57 | 40 | 45 | 22 | [80 empty] | Total Load R: 102; Total Load Y: 60; Total Load B: 85; Total Load N: 52 | 102 | 60 | 74.5544 | Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN2 | 23.393331, 56.717019 | 1093 | Ground (GMT) |  | 500 |  | 1 | [98 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN4 | 23.393452, 56.717699 | 1150 | Ground (GMT) |  | 500 | 21/05/2026, 08:55 | 1 | 237 | 237 | 235 | 410 | 411 | 409 | 185 mm² |  | 75 | 72 | 116 | 36 | 185 mm² |  | 115 | 47 | 35 | 38 | [80 empty] | Total Load R: 190; Total Load Y: 119; Total Load B: 151; Total Load N: 74 | 190 | 119 | 26.9854 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN4 | 23.394923, 56.994066 | 1148 | Ground (GMT) |  | 1000 | 21/05/2026, 08:52 | 1 | 242 | 243 | 241 | 419 | 422 | 420 | 240 mm² |  | 70 | 50 | 60 | 17 | 240 mm² |  | 137 | 118 | 63 | 58 | 240 mm² |  | 78 | 72 | 92 | 25 | [74 empty] | Total Load R: 285; Total Load Y: 240; Total Load B: 215; Total Load N: 100 | 285 | 215 | 20.6833 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.412368, 56.928075 | 2200 | Pole (PMT) |  | 100 |  | 1 | 230 | 233 | 232 | 401 | 401 | 402 | [92 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN7 | 23.396078, 56.917475 | 1466 | Pole (PMT) |  | 100 | 20/05/2026, 15:41 | 1 | 228 | 229 | 229 | 397 | 398 | 398 | 120 mm² |  | 40 | 56 | 20 | 32 | [86 empty] | Total Load R: 40; Total Load Y: 56; Total Load B: 20; Total Load N: 32 | 56 | 20 | 38.507 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.390728, 56.916822 | 1123 | Ground (GMT) |  | 500 | 20/05/2026, 15:31 | 1 | 228 | 231 | 228 | 392 | 400 | 395 | [6 empty] | 120 mm² |  | 94 | 55 | 159 | 87 | 120 mm² |  | 85 | 66 | 142 | 40 | 185 mm² |  | 77 | 55 | 129 | 57 | [68 empty] | Total Load R: 256; Total Load Y: 176; Total Load B: 430; Total Load N: 184 | 430 | 176 | 58.3909 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.390293, 56.920128 | 1793 | Pole (PMT) |  | 315 | 20/05/2026, 15:21 | 1 | 229 | 231 | 229 | 395 | 401 | 399 | 185 mm² |  | 74 | 81 | 130 | 43 | 185 mm² |  | 57 | 53 | 39 | 12 | [80 empty] | Total Load R: 131; Total Load Y: 134; Total Load B: 169; Total Load N: 55 | 169 | 131 | 36.7057 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.390164, 56.922854 | 1122 | Pole (PMT) |  | 315 | 20/05/2026, 15:08 | 1 | 240 | 242 | 241 | 416 | 419 | 417 | 120 mm² |  | 35 | 66 | 60 | 25 | 120 mm² |  | 149 | 107 | 114 | 35 | [80 empty] | Total Load R: 184; Total Load Y: 173; Total Load B: 174; Total Load N: 60 | 184 | 173 | 42.0883 | OK - No Upgrade | OK - Balanced
Hijermat | MAQNYAT | K_LN7 | 23.38888, 56.921707 | 1121 | Pole (PMT) |  | 315 | 20/05/2026, 15:03 | 1 | 227 | 231 | 230 | 395 | 399 | 394 | 185 mm² |  | 86 | 35 | 22 | 21 | 185 mm² |  | 182 | 121 | 138 | 45 | [80 empty] | Total Load R: 268; Total Load Y: 156; Total Load B: 160; Total Load N: 66 | 268 | 156 | 58.2079 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.387839, 56.920245 | 1451 | Pole (PMT) |  | 315 | 20/05/2026, 14:56 | 1 | 230 | 229 | 232 | 400 | 400 | 399 | 185 mm² |  | 10 | 4 | 6 | 8 | 185 mm² |  | 2004 | 200 | 178 | 37 | [80 empty] | Total Load R: 2014; Total Load Y: 204; Total Load B: 184; Total Load N: 45 | 2014 | 184 | 442.9651 | Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.385724, 56.919936 | 1120 | Ground (GMT) |  | 1000 | 20/05/2026, 14:50 | 1 | 231 | 233 | 233 | 401 | 404 | 401 | 120 mm² |  | 43 | 30 | 23 | 19 | [6 empty] | 185 mm² |  | 66 | 45 | 68 | 22 | 185 mm² |  | 196 | 111 | 120 | 65 | 185 mm² |  | 11 | 51 | 11 | 38 | [62 empty] | Total Load R: 316; Total Load Y: 237; Total Load B: 222; Total Load N: 144 | 316 | 222 | 21.9479 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.384489, 56.918189 | 1118 | Pole (PMT) |  | 315 | 20/05/2026, 14:39 | 1 | 230 | 231 | 231 | 400 | 400 | 400 | 185 mm² |  | 56 | 61 | 47 | 14 | 240 mm² |  | 28 | 59 | 50 | 23 | [80 empty] | Total Load R: 84; Total Load Y: 120; Total Load B: 97; Total Load N: 37 | 120 | 84 | 26.3932 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.382202, 56.916395 | 1117 | Pole (PMT) |  | 100 | 20/05/2026, 14:31 | 1 | 231 | 233 | 233 | 402 | 405 | 402 | 120 mm² |  | 13 | 3 | 5 | 8 | [86 empty] | Total Load R: 13; Total Load Y: 3; Total Load B: 5; Total Load N: 8 | 13 | 3 | 9.0517 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.381066, 56.916265 | 2150 | Pole (PMT) |  | 315 | 20/05/2026, 14:27 | 1 | 233 | 235 | 234 | 404 | 407 | 404 | 185 mm² |  | 15 | 9 | 8 | 8 | 185 mm² |  | 22 | 10 | 16 | 11 | [80 empty] | Total Load R: 37; Total Load Y: 19; Total Load B: 24; Total Load N: 19 | 37 | 19 | 8.2193 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.380159, 56.913137 | 1116 | Pole (PMT) |  | 100 | 20/05/2026, 14:17 | 1 | 232 | 234 | 236 | 406 | 406 | 402 | 120 mm² |  | 31 | 31 | 7 | 19 | 70 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 31; Total Load Y: 31; Total Load B: 7; Total Load N: 19 | 31 | 7 | 21.7996 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.380102, 56.910506 | 1711 | Pole (PMT) |  | 315 | 20/05/2026, 14:07 | 1 | 231 | 233 | 232 | 400 | 400 | 404 | 185 mm² |  | 70 | 60 | 122 | 59 | [86 empty] | Total Load R: 70; Total Load Y: 60; Total Load B: 122; Total Load N: 59 | 122 | 60 | 26.833 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.375508, 56.913971 | 4439 | Pole (PMT) |  | 100 | 20/05/2026, 14:01 | 1 | 222 | 223 | 223 | 385 | 385 | 388 | 185 mm² |  | 7 | 1 | 15 | 8 | [86 empty] | Total Load R: 7; Total Load Y: 1; Total Load B: 15; Total Load N: 8 | 15 | 1 | 10.0026 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.378567, 56.909735 | 1115 | Pole (PMT) |  | 315 | 20/05/2026, 13:53 | 1 | 233 | 234 | 235 | 404 | 405 | 404 | 120 mm² |  | 98 | 84 | 85 | 49 | [86 empty] | Total Load R: 98; Total Load Y: 84; Total Load B: 85; Total Load N: 49 | 98 | 84 | 21.77 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.377227, 56.90644 | 2149 | Pole (PMT) |  | 315 | 20/05/2026, 13:48 | 1 | 236 | 237 | 238 | 409 | 412 | 410 | 185 mm² |  | 12 | 15 | 10 | 8 | 185 mm² |  | 14 | 40 | 23 | 16 | [80 empty] | Total Load R: 26; Total Load Y: 55; Total Load B: 33; Total Load N: 24 | 55 | 26 | 12.369 | OK - No Upgrade | Need to Balance
Hijermat | MAQNYAT | K_LN7 | 23.377328, 56.903591 | 2372 | Pole (PMT) |  | 315 | 20/05/2026, 13:42 | 1 | 238 | 239 | 240 | 414 | 415 | 411 | 185 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 10 | 9 | 5 | 7 | [80 empty] | Total Load R: 10; Total Load Y: 9; Total Load B: 5; Total Load N: 7 | 10 | 5 | 2.2764 | OK - No Upgrade | Need to Balance

## 33KV feeder
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Hamra AlDaroo | 33KV feeder | K_LN1 | 22.447265, 56.70418 | 2 | Pole (PMT) |  | 315 | 20/05/2026, 15:00 | 1 | 257 | 256 | 257 | 444 | 442 | 443 | 120 mm² |  | 1 | 4 | 2 | 8 | [14 empty] | Total Load R: 1; Total Load Y: 4; Total Load B: 2; Total Load N: 8 | 4 | 1 | 0.97655 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | 33KV feeder | K_LN1 | 22.609313, 56.716692 | 1 | Pole (PMT) |  | 100 | 20/05/2026, 14:39 | 1 | 241 | 241 | 242 | 417 | 418 | 418 | 120 mm² |  | 2 | 2 | 1 | 1 | [14 empty] | Total Load R: 2; Total Load Y: 2; Total Load B: 1; Total Load N: 1 | 2 | 1 | 1.4445 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | 33KV feeder | K_LN1 | 22.704347, 56.641546 | 3 | Pole (PMT) |  | 100 | 20/05/2026, 13:48 | 1 | 246 | 246 | 247 | 425 | 427 | 427 | 120 mm² |  | 4 | 2 | 1 | 5 | [14 empty] | Total Load R: 4; Total Load Y: 2; Total Load B: 1; Total Load N: 5 | 4 | 1 | 2.9445 | OK - No Upgrade | Need to Balance

## Zubra
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Hamra AlDaroo | Zubra | K_LN1 | 22.593669, 56.691762 | 3 | Pole (PMT) |  | 100 | 20/05/2026, 14:31 | 1 | 252 | 248 | 253 | 427 | 430 | 438 |  |  | 2 | 1 | 1 | 1 | [14 empty] | Total Load R: 2; Total Load Y: 1; Total Load B: 1; Total Load N: 1 | 2 | 1 | 1.4792 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Zubra | K_LN1 | 22.605914, 56.69632 | 1 | Pole (PMT) |  | 200 | 20/05/2026, 14:25 | 1 | 252 | 253 | 252 | 436 | 437 | 438 | 120 mm² |  | 2 | 4 | 24 | 42 | 120 mm² |  | 9 | 3 | 47 | 39 | [8 empty] | Total Load R: 11; Total Load Y: 7; Total Load B: 71; Total Load N: 81 | 71 | 7 | 26.8087 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Zubra | K_LN1 | 22.63607, 56.698305 | 4 | Pole (PMT) |  | 100 | 20/05/2026, 14:11 | 1 | 240 | 241 | 242 | 407 | 412 | 418 | 120 mm² |  | 4 | 1 | 2 | 1 | [14 empty] | Total Load R: 4; Total Load Y: 1; Total Load B: 2; Total Load N: 1 | 4 | 1 | 2.8198 | OK - No Upgrade | Need to Balance
Hamra AlDaroo | Zubra | K_LN1 | 22.672946, 56.700294 | 2 | Pole (PMT) |  | 100 | 20/05/2026, 14:01 | 1 | 249 | 252 | 250 | 432 | 431 | 436 | 120 mm² |  | 39 | 6 | 44 | 34 | 120 mm² |  | 0 | 0 | 0 | 0 | [8 empty] | Total Load R: 39; Total Load Y: 6; Total Load B: 44; Total Load N: 34 | 44 | 6 | 32.9228 | OK - No Upgrade | Need to Balance

## AL-NUJAYD
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Hijermat | AL-NUJAYD | K_LN03 | 23.434442, 56.774577 | 1062 | Pole (PMT) | 3 | 200 | 11/06/2026, 17:22 | 1 | 235 | 236 | 236 | 410 | 411 | 410 | 185 mm² |  | 10 | 15 | 5 | 10 | 185 mm² |  | 28 | 30 | 40 | 22 | [32 empty] | Total Load R: 38; Total Load Y: 45; Total Load B: 45; Total Load N: 32 | 45 | 38 | 15.9782 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN03 | 23.45579, 56.791217 | 4348 | Pole (PMT) | 3 | 100 | 11/06/2026, 16:33 | 1 | 240 | 240 | 241 | 420 | 421 | 421 | 120 mm² |  | 10 | 11 | 9 | 9 | [38 empty] | Total Load R: 10; Total Load Y: 11; Total Load B: 9; Total Load N: 9 | 11 | 9 | 8.0021 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN03 | 23.455737, 56.791033 | 1058 | Pole (PMT) | 3 | 200 | 11/06/2026, 16:32 | 1 | 239 | 240 | 241 | 425 | 424 | 423 | 120 mm² |  | 14 | 16 | 15 | 11 | 120 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 14; Total Load Y: 16; Total Load B: 15; Total Load N: 11 | 16 | 14 | 5.889 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN03 | 23.458273, 56.793872 | 2105 | Pole (PMT) | 3 | 200 | 11/06/2026, 16:26 | 1 | 240 | 241 | 242 | 420 | 421 | 421 | 120 mm² |  | 11 | 10 | 9 | 8 | [38 empty] | Total Load R: 11; Total Load Y: 10; Total Load B: 9; Total Load N: 8 | 11 | 9 | 4.001 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN03 | 23.460231, 56.794767 | 1302 | Pole (PMT) | 3 | 100 | 11/06/2026, 16:23 | 1 | 240 | 241 | 243 | 419 | 418 | 419 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 10 | 11 | 12 | 9 | [32 empty] | Total Load R: 10; Total Load Y: 11; Total Load B: 12; Total Load N: 9 | 12 | 10 | 8.7088 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN03 | 23.471026, 56.799511 | 1520 | Pole (PMT) | 3 | 200 | 11/06/2026, 16:17 | 1 | 247 | 246 | 248 | 427 | 428 | 426 | 185 mm² |  | 0 | 10 | 0 | 12 | 185 mm² |  | 68 | 117 | 51 | 51 | [32 empty] | Total Load R: 68; Total Load Y: 127; Total Load B: 51; Total Load N: 63 | 127 | 51 | 46.9637 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.467222, 56.800218 | 1057 | Ground (GMT) | 3 | 1000 | 11/06/2026, 16:12 | 1 | 246 | 246 | 246 | 427 | 426 | 426 | [30 empty] | 185 mm² |  | 95 | 100 | 66 | 29 | 185 mm² |  | 131 | 38 | 77 | 30 | 185 mm² |  | 69 | 35 | 40 | 20 | 295 | 173 | 183 | 79 | 295 | 173 | 21.8178 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.463954, 56.798487 | 1407 | Ground (GMT) | 3 | 500 | 11/06/2026, 16:03 | 1 | 245 | 245 | 245 | 423 | 424 | 244 | [12 empty] | 185 mm² |  | 81 | 78 | 83 | 15 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 74 | 62 | 23 | 16 | 185 mm² |  | 20 | 23 | 23 | 0 | [6 empty] | 185 mm² |  | 28 | 15 | 74 | 45 | 203 | 178 | 203 | 76 | 203 | 178 | 29.7459 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN03 | 23.463429, 56.7976 | 1055 | Ground (GMT) | 3 | 1000 | 11/06/2026, 15:54 | 1 | 244 | 243 | 244 | 421 | 422 | 422 | [12 empty] | 185 mm² |  | 83 | 78 | 93 | 0 | 185 mm² |  | 119 | 47 | 97 | 51 | 185 mm² |  | 213 | 198 | 261 | 57 | 240 mm² |  | 16 | 32 | 12 | 16 | [8 empty] | Total Load R: 431; Total Load Y: 355; Total Load B: 463; Total Load N: 124 | 463 | 355 | 33.7617 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.46034, 56.799971 | 000 | Pole (PMT) | 3 | 315 | 11/06/2026, 15:47 | 1 | 244 | 243 | 246 | 422 | 425 | 422 | 185 mm² |  | 58 | 70 | 34 | 31 | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 58; Total Load Y: 70; Total Load B: 34; Total Load N: 31 | 70 | 34 | 16.2428 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.45356, 56.795907 | 1962 | Pole (PMT) | 3 | 315 | 11/06/2026, 15:36 | 1 | 243 | 243 | 243 | 420 | 421 | 420 | 185 mm² |  | 32 | 26 | 19 | 15 | 185 mm² |  | 17 | 21 | 35 | 14 | [32 empty] | Total Load R: 49; Total Load Y: 47; Total Load B: 54; Total Load N: 29 | 54 | 47 | 12.4708 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN03 | 23.451087, 56.793902 | 4678 | Pole (PMT) | 3 | 100 | 11/06/2026, 15:30 | 1 | 243 | 243 | 243 | 419 | 421 | 240 | 185 mm² |  | 28 | 11 | 11 | 13 | [38 empty] | Total Load R: 28; Total Load Y: 11; Total Load B: 11; Total Load N: 13 | 28 | 11 | 20.3204 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.447616, 56.788687 | 1059 | Pole (PMT) | 3 | 100 | 11/06/2026, 15:25 | 1 | 240 | 241 | 241 | 420 | 421 | 422 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN03 | 23.447603, 56.7892 | 2249 | Pole (PMT) | 3 | 315 | 11/06/2026, 15:22 | 1 | 241 | 241 | 242 | 417 | 419 | 418 | 185 mm² |  | 0 | 0 | 14 | 0 | 185 mm² |  | 77 | 14 | 35 | 49 | [32 empty] | Total Load R: 77; Total Load Y: 14; Total Load B: 49; Total Load N: 49 | 77 | 14 | 17.6554 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.441458, 56.782622 | 1060 | Pole (PMT) | 3 | 315 | 11/06/2026, 15:17 | 1 | 234 | 235 | 236 | 403 | 407 | 406 | 120 mm² |  | 67 | 41 | 40 | 22 | 120 mm² |  | 265 | 165 | 173 | 89 | [32 empty] | Total Load R: 332; Total Load Y: 206; Total Load B: 213; Total Load N: 111 | 332 | 206 | 73.5687 | Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.436907, 56.787386 | 1701 | Pole (PMT) | 3 | 100 | 11/06/2026, 17:38 | 1 | 225 | 225 | 226 | 399 | 398 | 397 | 185 mm² |  | 9 | 8 | 6 | 5 | 120 mm² |  | 150 | 145 | 160 | 45 | [32 empty] | Total Load R: 159; Total Load Y: 153; Total Load B: 166; Total Load N: 50 | 166 | 153 | 114.7207 | Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN03 | 23.436878, 56.787509 | 4438 | Pole (PMT) | 3 | 100 | 11/06/2026, 17:31 | 1 | 226 | 225 | 224 | 400 | 399 | 398 | 120 mm² |  | 5 | 6 | 5 | 4 | [38 empty] | Total Load R: 5; Total Load Y: 6; Total Load B: 5; Total Load N: 4 | 6 | 5 | 4.1569 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.436878, 56.787509 | 1067 | Pole (PMT) | 3 | 100 | 11/06/2026, 17:28 | 1 | 225 | 226 | 227 | 400 | 399 | 401 | 185 mm² |  | 40 | 30 | 35 | 25 | [38 empty] | Total Load R: 40; Total Load Y: 30; Total Load B: 35; Total Load N: 25 | 40 | 30 | 27.7128 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.436892, 56.787546 | 2108 | Pole (PMT) | 3 | 315 | 11/06/2026, 17:41 | 1 | 235 | 236 | 236 | 419 | 418 | 417 | 185 mm² |  | 80 | 70 | 66 | 31 | [38 empty] | Total Load R: 80; Total Load Y: 70; Total Load B: 66; Total Load N: 31 | 80 | 66 | 18.4312 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.436914, 56.77822 | 1061 | Pole (PMT) | 3 | 100 | 11/06/2026, 14:52 | 1 | 240 | 241 | 242 | 415 | 417 | 416 | 70 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN03 | 23.437391, 56.789997 | 2170 | Pole (PMT) | 3 | 315 | 11/06/2026, 14:45 | 1 | 234 | 234 | 235 | 403 | 406 | 405 | 185 mm² |  | 148 | 115 | 93 | 51 | 185 mm² |  | 55 | 34 | 23 | 27 | [32 empty] | Total Load R: 203; Total Load Y: 149; Total Load B: 116; Total Load N: 78 | 203 | 116 | 44.9833 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.439777, 56.792524 | 1514 | Pole (PMT) | 3 | 100 | 11/06/2026, 14:40 | 1 | 230 | 232 | 231 | 398 | 400 | 399 | 120 mm² |  | 77 | 67 | 45 | 23 | 120 mm² |  | 28 | 21 | 36 | 15 | [32 empty] | Total Load R: 105; Total Load Y: 88; Total Load B: 81; Total Load N: 38 | 105 | 81 | 72.3824 | Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.436693, 56.786544 | 1065 | Pole (PMT) | 3 | 315 | 11/06/2026, 14:31 | 1 | 233 | 234 | 235 | 401 | 405 | 406 | 120 mm² |  | 275 | 171 | 230 | 68 | 120 mm² |  | 29 | 57 | 24 | 32 | 120 mm² |  | 0 | 0 | 0 | 0 | [26 empty] | Total Load R: 304; Total Load Y: 228; Total Load B: 254; Total Load N: 100 | 304 | 228 | 67.0298 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.433144, 56.792465 | 4531 | Pole (PMT) | 3 | 200 | 11/06/2026, 14:24 | 1 | 236 | 233 | 230 | 407 | 407 | 409 | 120 mm² |  | 12 | 61 | 0 | 52 | 120 mm² |  | 35 | 65 | 100 | 48 | [32 empty] | Total Load R: 47; Total Load Y: 126; Total Load B: 100; Total Load N: 100 | 126 | 47 | 44.4115 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.435797, 56.793331 | 1066 | Pole (PMT) | 3 | 315 | 11/06/2026, 14:11 | 1 | 236 | 237 | 240 | 408 | 412 | 411 | 120 mm² |  | 100 | 52 | 40 | 43 | 240 mm² |  | 42 | 0 | 21 | 26 | [32 empty] | Total Load R: 142; Total Load Y: 52; Total Load B: 61; Total Load N: 69 | 142 | 52 | 31.8565 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.424877, 56.788634 | 1457 | Pole (PMT) | 3 | 100 | 11/06/2026, 14:05 | 1 | 246 | 246 | 249 | 425 | 420 | 428 | 120 mm² |  | 59 | 45 | 39 | 18 | [38 empty] | Total Load R: 59; Total Load Y: 45; Total Load B: 39; Total Load N: 18 | 59 | 39 | 43.4312 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.43126, 56.78635 | 1064 | Pole (PMT) | 3 | 315 | 11/06/2026, 14:02 | 1 | 232 | 237 | 239 | 412 | 413 | 412 | 120 mm² |  | 37 | 37 | 63 | 29 | [38 empty] | Total Load R: 37; Total Load Y: 37; Total Load B: 63; Total Load N: 29 | 63 | 37 | 14.2721 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN03 | 23.4342, 56.787514 | 4743 | Pole (PMT) | 3 | 100 | 11/06/2026, 13:58 | 1 | 239 | 240 | 241 | 416 | 417 | 418 | 185 mm² |  | 12 | 11 | 10 | 8 | [38 empty] | Total Load R: 12; Total Load Y: 11; Total Load B: 10; Total Load N: 8 | 12 | 10 | 8.6464 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN03 | 23.432869, 56.779729 | 1063 | Pole (PMT) | 3 | 315 | 11/06/2026, 13:55 | 1 | 236 | 235 | 238 | 407 | 411 | 409 | 240 mm² |  | 113 | 149 | 130 | 28 | 120 mm² |  | 82 | 46 | 25 | 51 | [32 empty] | Total Load R: 195; Total Load Y: 195; Total Load B: 155; Total Load N: 79 | 195 | 155 | 43.6394 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN03 | 23.434138, 56.774072 | 1077 | Ground (GMT) | 3 | 1000 | 11/06/2026, 13:49 | 1 | 238 | 239 | 238 | 413 | 413 | 416 | [12 empty] | 185 mm² |  | 153 | 128 | 101 | 80 | 185 mm² |  | 198 | 81 | 135 | 98 | 185 mm² |  | 47 | 48 | 58 | 11 | 185 mm² |  | 12 | 43 | 26 | 20 | [8 empty] | Total Load R: 410; Total Load Y: 300; Total Load B: 320; Total Load N: 209 | 410 | 300 | 29.3288 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.458763, 56.931283 | 2025 | Pole (PMT) | 3 | 100 | 08/06/2026, 13:35 | 1 | 234 | 238 | 236 | 415 | 414 | 416 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.462149, 56.912658 | 999 | Pole (PMT) | 3 | 100 | 08/06/2026, 13:33 | 1 | 241 | 239 | 239 | 417 | 416 | 415 | 120 mm² |  | 12 | 10 | 25 | 16 | 120 mm² |  | 10 | 12 | 11 | 8 | [32 empty] | Total Load R: 22; Total Load Y: 22; Total Load B: 36; Total Load N: 24 | 36 | 22 | 26.0015 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.469628, 56.908047 | 998 | Pole (PMT) | 3 | 100 | 08/06/2026, 13:30 | 1 | 241 | 243 | 241 | 414 | 415 | 413 | 120 mm² |  | 30 | 22 | 48 | 15 | [38 empty] | Total Load R: 30; Total Load Y: 22; Total Load B: 48; Total Load N: 15 | 48 | 22 | 34.4193 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.471443, 56.903356 | 997 | Pole (PMT) | 3 | 100 | 08/06/2026, 13:28 | 1 | 240 | 242 | 241 | 415 | 416 | 414 | 120 mm² |  | 51 | 58 | 63 | 14 | [38 empty] | Total Load R: 51; Total Load Y: 58; Total Load B: 63; Total Load N: 14 | 63 | 51 | 45.2845 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.473963, 56.895067 | 4516 | Pole (PMT) | 3 | 100 | 08/06/2026, 13:26 | 1 | 239 | 237 | 238 | 412 | 413 | 413 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.474593, 56.891316 | 996 | Pole (PMT) | 3 | 100 | 08/06/2026, 13:23 | 1 | 241 | 243 | 244 | 413 | 414 | 413 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.476508, 56.882332 | 4724 | Pole (PMT) | 3 | 100 | 08/06/2026, 13:19 | 1 | 240 | 242 | 241 | 411 | 413 | 416 | 120 mm² |  | 10 | 0 | 0 | 8 | [38 empty] | Total Load R: 10; Total Load Y: 0; Total Load B: 0; Total Load N: 8 | 10 | 0 | 7.1187 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.484875, 57.042927 | 1030 | Pole (PMT) |  | 100 | 03/06/2026, 15:05 | 1 | 235 | 235 | 236 | 407 | 408 | 402 | 50 mm² |  | 7 | 8 | 2 | 5 | [38 empty] | Total Load R: 7; Total Load Y: 8; Total Load B: 2; Total Load N: 5 | 8 | 2 | 5.6396 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.484013, 57.041873 | 1034 | Pole (PMT) |  | 100 | 03/06/2026, 15:03 | 1 | 246 | 247 | 245 | 424 | 429 | 428 | 120 mm² |  | 15 | 17 | 42 | 24 | [38 empty] | Total Load R: 15; Total Load Y: 17; Total Load B: 42; Total Load N: 24 | 42 | 15 | 30.8444 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.484343, 57.043337 | 1035 | Pole (PMT) |  | 315 | 03/06/2026, 15:01 | 1 | 239 | 239 | 240 | 416 | 416 | 414 | 185 mm² |  | 10 | 25 | 20 | 19 | 120 mm² |  | 8 | 24 | 13 | 15 | [32 empty] | Total Load R: 18; Total Load Y: 49; Total Load B: 33; Total Load N: 34 | 49 | 18 | 11.2083 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.482395, 57.04335 | 1036 | Pole (PMT) |  | 200 | 03/06/2026, 14:59 | 1 | 238 | 235 | 239 | 413 | 410 | 412 | 120 mm² |  | 50 | 88 | 61 | 38 | 120 mm² |  | 1 | 3 | 2 | 4 | [32 empty] | Total Load R: 51; Total Load Y: 91; Total Load B: 63; Total Load N: 42 | 91 | 51 | 32.5478 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.48253, 57.041734 | 4641 | Pole (PMT) |  | 100 | 03/06/2026, 14:57 | 1 | 239 | 241 | 240 | 414 | 417 | 415 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.480654, 57.042324 | 4271 | Pole (PMT) |  | 100 | 03/06/2026, 14:55 | 1 | 239 | 240 | 230 | 413 | 416 | 415 | 120 mm² |  | 4 | 0 | 19 | 11 | [38 empty] | Total Load R: 4; Total Load Y: 0; Total Load B: 19; Total Load N: 11 | 19 | 0 | 13.5914 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.482526, 57.039725 | 1033 | Pole (PMT) |  | 200 | 03/06/2026, 14:53 | 1 | 234 | 236 | 236 | 406 | 409 | 406 | 120 mm² |  | 146 | 112 | 117 | 28 | [38 empty] | Total Load R: 146; Total Load Y: 112; Total Load B: 117; Total Load N: 28 | 146 | 112 | 51.3345 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.48166, 57.038807 | 1547 | Pole (PMT) |  | 100 | 03/06/2026, 14:51 | 1 | 235 | 238 | 237 | 410 | 411 | 409 | 120 mm² |  | 39 | 25 | 36 | 14 | [38 empty] | Total Load R: 39; Total Load Y: 25; Total Load B: 36; Total Load N: 14 | 39 | 25 | 27.6955 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.481074, 57.035562 | 1749 | Pole (PMT) |  | 100 | 03/06/2026, 14:49 | 1 | 238 | 241 | 239 | 412 | 415 | 414 | 185 mm² |  | 29 | 13 | 30 | 18 | [38 empty] | Total Load R: 29; Total Load Y: 13; Total Load B: 30; Total Load N: 18 | 30 | 13 | 21.4081 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.48564, 56.999164 | 1028 | Pole (PMT) |  | 100 | 03/06/2026, 14:47 | 1 | 236 | 238 | 237 | 410 | 413 | 409 | 120 mm² |  | 5 | 8 | 7 | 10 | 120 mm² |  | 119 | 77 | 121 | 40 | [32 empty] | Total Load R: 124; Total Load Y: 85; Total Load B: 128; Total Load N: 50 | 128 | 85 | 90.898 | Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.490661, 56.990035 | 1032 | Pole (PMT) |  | 315 | 03/06/2026, 14:45 | 1 | 238 | 239 | 238 | 411 | 412 | 414 | 120 mm² |  | 92 | 98 | 97 | 21 | [38 empty] | Total Load R: 92; Total Load Y: 98; Total Load B: 97; Total Load N: 21 | 98 | 92 | 22.1472 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.487775, 57.001865 | 1029 | Pole (PMT) |  | 100 | 03/06/2026, 14:43 | 1 | 231 | 237 | 234 | 404 | 408 | 403 | 120 mm² |  | 125 | 69 | 60 | 51 | [38 empty] | Total Load R: 125; Total Load Y: 69; Total Load B: 60; Total Load N: 51 | 125 | 60 | 87.4686 | Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.489077, 57.011126 | 1487 | Pole (PMT) |  | 100 | 03/06/2026, 14:41 | 1 | 233 | 237 | 237 | 407 | 410 | 404 | 120 mm² |  | 79 | 55 | 28 | 47 | [38 empty] | Total Load R: 79; Total Load Y: 55; Total Load B: 28; Total Load N: 47 | 79 | 28 | 55.6906 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.491553, 56.999804 | 1504 | Pole (PMT) |  | 100 | 03/06/2026, 14:40 | 1 | 240 | 238 | 245 | 410 | 411 | 415 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.489366, 57.001863 | 1894 | Pole (PMT) |  | 315 | 03/06/2026, 14:38 | 1 | 237 | 239 | 238 | 411 | 413 | 413 | 185 mm² |  | 11 | 6 | 10 | 15 | 185 mm² |  | 24 | 24 | 12 | 13 | [32 empty] | Total Load R: 35; Total Load Y: 30; Total Load B: 22; Total Load N: 28 | 35 | 22 | 7.9097 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.48725, 56.969671 | 1026 | Pole (PMT) |  | 100 | 03/06/2026, 14:36 | 1 | 238 | 239 | 238 | 411 | 413 | 414 | 120 mm² |  | 29 | 32 | 25 | 10 | 120 mm² |  | 20 | 8 | 32 | 10 | [32 empty] | Total Load R: 49; Total Load Y: 40; Total Load B: 57; Total Load N: 20 | 57 | 40 | 40.5768 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.488719, 56.984001 | 1027 | Pole (PMT) |  | 200 | 03/06/2026, 14:34 | 1 | 241 | 240 | 243 | 410 | 413 | 415 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.487145, 57.00422 | 1682 | Pole (PMT) |  | 100 | 03/06/2026, 14:32 | 1 | 246 | 247 | 248 | 424 | 426 | 428 | 120 mm² |  | 5 | 12 | 19 | 14 | [38 empty] | Total Load R: 5; Total Load Y: 12; Total Load B: 19; Total Load N: 14 | 19 | 5 | 13.9534 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.493066, 56.981119 | 1025 | Pole (PMT) |  | 200 | 03/06/2026, 14:31 | 1 | 241 | 242 | 241 | 417 | 419 | 417 | 120 mm² |  | 85 | 67 | 57 | 35 | [38 empty] | Total Load R: 85; Total Load Y: 67; Total Load B: 57; Total Load N: 35 | 85 | 57 | 30.6963 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.489454, 56.967107 | 1023 | Pole (PMT) |  | 100 | 03/06/2026, 14:29 | 1 | 240 | 241 | 240 | 416 | 419 | 416 | 120 mm² |  | 11 | 5 | 3 | 7 | 185 mm² |  | 9 | 13 | 27 | 14 | [32 empty] | Total Load R: 20; Total Load Y: 18; Total Load B: 30; Total Load N: 21 | 30 | 18 | 21.616 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.48641, 56.951484 | 4354 | Pole (PMT) |  | 50 | 03/06/2026, 14:27 | 1 | 241 | 243 | 244 | 415 | 420 | 422 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.493663, 56.939774 | 1655 | Pole (PMT) |  | 100 | 03/06/2026, 14:25 | 1 | 243 | 243 | 244 | 420 | 421 | 421 | 185 mm² |  | 39 | 60 | 42 | 21 | [38 empty] | Total Load R: 39; Total Load Y: 60; Total Load B: 42; Total Load N: 21 | 60 | 39 | 43.6477 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.494778, 56.938967 | 1021 | Pole (PMT) |  | 315 | 03/06/2026, 14:23 | 1 | 243 | 244 | 242 | 421 | 420 | 423 | 120 mm² |  | 55 | 70 | 56 | 11 | [38 empty] | Total Load R: 55; Total Load Y: 70; Total Load B: 56; Total Load N: 11 | 70 | 55 | 16.2043 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.498077, 56.938969 | 1629 | Pole (PMT) |  | 100 | 03/06/2026, 14:22 | 1 | 243 | 244 | 244 | 422 | 423 | 421 | 120 mm² |  | 25 | 13 | 10 | 10 | [38 empty] | Total Load R: 25; Total Load Y: 13; Total Load B: 10; Total Load N: 10 | 25 | 10 | 18.2731 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.501104, 56.929581 | 2061 | Pole (PMT) |  | 100 | 03/06/2026, 14:20 | 1 | 246 | 245 | 245 | 423 | 424 | 427 | 185 mm² |  | 3 | 14 | 11 | 9 | [38 empty] | Total Load R: 3; Total Load Y: 14; Total Load B: 11; Total Load N: 9 | 14 | 3 | 10.2572 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.502888, 56.925976 | 1020 | Pole (PMT) |  | 315 | 03/06/2026, 14:18 | 1 | 244 | 245 | 245 | 425 | 423 | 422 | 120 mm² |  | 68 | 102 | 75 | 33 | [38 empty] | Total Load R: 68; Total Load Y: 102; Total Load B: 75; Total Load N: 33 | 102 | 68 | 23.8363 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.513701, 56.943786 | 1963 | Pole (PMT) |  | 100 | 02/06/2026, 14:26 | 1 | 246 | 245 | 243 | 425 | 423 | 422 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.514646, 56.911191 | 1579 | Pole (PMT) |  | 100 | 02/06/2026, 14:21 | 1 | 245 | 246 | 244 | 426 | 420 | 424 | 120 mm² |  | 11 | 11 | 19 | 0 | 120 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 11; Total Load Y: 11; Total Load B: 19; Total Load N: 0 | 19 | 11 | 14.0192 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.525828, 56.922198 | 4745 | Pole (PMT) |  | 200 | 02/06/2026, 14:19 | 1 | 243 | 243 | 244 | 422 | 421 | 422 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 10 | 38 | 11 | 22 | [32 empty] | Total Load R: 10; Total Load Y: 38; Total Load B: 11; Total Load N: 22 | 38 | 10 | 13.8876 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.514243, 56.940842 | 1805 | Pole (PMT) |  | 315 | 02/06/2026, 14:17 | 1 | 241 | 244 | 241 | 420 | 417 | 418 | 120 mm² |  | 26 | 11 | 19 | 10 | 120 mm² |  | 65 | 77 | 39 | 29 | [32 empty] | Total Load R: 91; Total Load Y: 88; Total Load B: 58; Total Load N: 39 | 91 | 58 | 21.0155 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.525516, 56.933511 | 1580 | Pole (PMT) |  | 315 | 02/06/2026, 14:15 | 1 | 242 | 243 | 243 | 418 | 417 | 415 | 185 mm² |  | 79 | 113 | 122 | 52 | 185 mm² |  | 64 | 49 | 64 | 21 | [32 empty] | Total Load R: 143; Total Load Y: 162; Total Load B: 186; Total Load N: 73 | 186 | 143 | 42.7503 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.524693, 56.925464 | 1047 | Pole (PMT) |  | 315 | 02/06/2026, 14:13 | 1 | 244 | 245 | 243 | 427 | 425 | 423 | 120 mm² |  | 50 | 48 | 120 | 48 | 120 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 50; Total Load Y: 48; Total Load B: 120; Total Load N: 48 | 120 | 48 | 28.1747 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.491488, 56.862854 | 2273 | Pole (PMT) |  | 315 | 25/05/2026, 16:00 | 1 | 222 | 223 | 224 | 384 | 388 | 389 | 185 mm² |  | 11 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 11; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 11 | 0 | 2.3226 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.51865, 56.927835 | 4403 | Pole (PMT) |  | 100 | 25/05/2026, 15:51 | 1 | 245 | 246 | 244 | 426 | 422 | 424 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN1 | 23.535024, 56.831859 | 2314 | Pole (PMT) |  | 100 | 25/05/2026, 14:09 | 1 | 238 | 237 | 238 | 414 | 412 | 413 | 120 mm² | [5 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.493213, 56.852053 | 2135 | Ground (GMT) |  | 1000 | 25/05/2026, 13:54 | 1 | 231 | 234 | 230 | 400 | 404 | 401 | 185 mm² |  | 51 | 27 | 12 | 17 | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 51; Total Load Y: 27; Total Load B: 12; Total Load N: 17 | 51 | 12 | 3.5334 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.498176, 56.857518 | 2120 | Pole (PMT) |  | 315 | 25/05/2026, 13:49 | 1 | 234 | 237 | 238 | 406 | 409 | 413 | 185 mm² |  | 13 | 0 | 0 | 11 | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 13; Total Load Y: 0; Total Load B: 0; Total Load N: 11 | 13 | 0 | 2.9021 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.499112, 56.859313 | 1575 | Pole (PMT) |  | 315 |  | 1 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.498987, 56.850785 | 2136 | Ground (GMT) |  | 1000 |  | 1 | 231 | 234 | 236 | 402 | 406 | 409 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.538523, 56.908966 | 1050 | Pole (PMT) |  | 100 | 24/05/2026, 17:39 | 1 | 241 | 238 | 244 | 427 | 425 | 429 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.402344, 56.727973 | 1046 | Pole (PMT) |  | 100 | 24/05/2026, 17:37 | 1 | 241 | 242 | 240 | 428 | 429 | 427 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.402344, 56.727973 | 1037 | Pole (PMT) |  | 315 | 24/05/2026, 17:33 | 1 | 242 | 247 | 248 | 422 | 424 | 429 | 240 mm² |  | 18 | 12 | 18 | 0 | 185 mm² |  | 173 | 128 | 71 | 84 | [32 empty] | Total Load R: 191; Total Load Y: 140; Total Load B: 89; Total Load N: 84 | 191 | 89 | 44.3196 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.402344, 56.727973 | 1049 | Pole (PMT) |  | 315 | 24/05/2026, 17:28 | 1 | 245 | 244 | 245 | 422 | 423 | 422 | 120 mm² |  | 20 | 86 | 50 | 50 | [38 empty] | Total Load R: 20; Total Load Y: 86; Total Load B: 50; Total Load N: 50 | 86 | 20 | 19.9554 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.402344, 56.727973 | 1505 | Pole (PMT) |  | 100 | 24/05/2026, 17:23 | 1 | 243 | 243 | 246 | 420 | 419 | 418 | 120 mm² |  | 50 | 38 | 50 | 12 | [38 empty] | Total Load R: 50; Total Load Y: 38; Total Load B: 50; Total Load N: 12 | 50 | 38 | 36.3731 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.402344, 56.727973 | 1044 | Pole (PMT) |  | 100 | 24/05/2026, 17:22 | 1 | 243 | 242 | 242 | 419 | 419 | 418 | 185 mm² |  | 50 | 56 | 39 | 22 | 120 mm² |  | 0 | 13 | 13 | 13 | [32 empty] | Total Load R: 50; Total Load Y: 69; Total Load B: 52; Total Load N: 35 | 69 | 50 | 50.0753 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.402494, 56.728025 | 1042 | Pole (PMT) |  | 100 | 24/05/2026, 17:20 | 1 | 246 | 244 | 244 | 423 | 423 | 422 | 120 mm² |  | 16 | 47 | 63 | 44 | [38 empty] | Total Load R: 16; Total Load Y: 47; Total Load B: 63; Total Load N: 44 | 63 | 16 | 46.1574 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.519301, 56.88839 | 1043 | Pole (PMT) |  | 200 | 24/05/2026, 17:12 | 1 | 246 | 246 | 247 | 427 | 128 | 428 | 185 mm² |  | 44 | 24 | 28 | 28 | 185 mm² |  | 51 | 46 | 13 | 41 | [32 empty] | Total Load R: 95; Total Load Y: 70; Total Load B: 41; Total Load N: 69 | 95 | 41 | 35.1303 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.519301, 56.88839 | 4511 | Pole (PMT) |  | 100 | 24/05/2026, 16:50 | 1 | 241 | 242 | 238 | 429 | 425 | 427 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.583784, 56.882196 | 04668 | Pole (PMT) |  | 100 | 24/05/2026, 16:32 | 1 | 243 | 244 | 244 | 421 | 422 | 424 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.583784, 56.882196 | 1054 | Pole (PMT) |  | 100 | 24/05/2026, 16:24 | 1 | 243 | 244 | 242 | 425 | 427 | 426 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.583784, 56.882196 | 1669 | Pole (PMT) |  | 50 | 24/05/2026, 16:23 | 1 | 244 | 243 | 243 | 426 | 424 | 425 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.583784, 56.882196 | 1053 | Pole (PMT) |  | 100 | 24/05/2026, 16:22 | 1 | 244 | 243 | 243 | 426 | 424 | 425 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.583784, 56.882196 | 4311 | Pole (PMT) |  | 100 | 24/05/2026, 16:20 | 1 | 244 | 243 | 243 | 426 | 424 | 425 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.583784, 56.882196 | 1052 | Pole (PMT) |  | 200 | 24/05/2026, 16:18 | 1 | 244 | 243 | 243 | 426 | 424 | 426 | 120 mm² |  | 0 | 12 | 13 | 0 | 240 mm² |  | 0 | 0 | 23 | 22 | [32 empty] | Total Load R: 0; Total Load Y: 12; Total Load B: 36; Total Load N: 22 | 36 | 0 | 13.2814 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.57841, 56.885274 | 1670 | Pole (PMT) |  | 100 | 24/05/2026, 16:03 | 1 | 243 | 244 | 244 | 426 | 424 | 423 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.565649, 56.897591 | 1051 | Pole (PMT) |  | 315 | 24/05/2026, 15:50 | 1 | 243 | 244 | 244 | 421 | 422 | 424 | 185 mm² |  | 29 | 37 | 13 | 19 |  |  | 45 | 57 | 59 | 13 | [32 empty] | Total Load R: 74; Total Load Y: 94; Total Load B: 72; Total Load N: 32 | 94 | 72 | 21.7601 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.565649, 56.897591 | 2143 | Pole (PMT) |  | 100 | 24/05/2026, 15:43 | 1 | 243 | 244 | 243 | 422 | 426 | 423 | 185 mm² |  | 10 | 0 | 29 | 22 | [38 empty] | Total Load R: 10; Total Load Y: 0; Total Load B: 29; Total Load N: 22 | 29 | 0 | 21.1968 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.565649, 56.897591 | 4252 | Pole (PMT) |  | 50 | 24/05/2026, 15:40 | 1 | 238 | 242 | 249 | 428 | 430 | 429 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.512111, 56.864931 | 1041 | Pole (PMT) |  | 500 | 24/05/2026, 15:00 | 1 | 244 | 245 | 245 | 423 | 424 | 424 | 185 mm² |  | 63 | 17 | 63 | 46 | 185 mm² |  | 45 | 43 | 12 | 37 | [32 empty] | Total Load R: 108; Total Load Y: 60; Total Load B: 75; Total Load N: 83 | 108 | 60 | 15.8254 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.512111, 56.864931 | 2014 | Pole (PMT) |  | 315 | 24/05/2026, 14:54 | 1 | 247 | 245 | 246 | 426 | 428 | 426 | 120 mm² |  | 0 | 0 | 0 | 0 | 70 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.512111, 56.864931 | 1874 | Pole (PMT) |  | 100 | 24/05/2026, 14:50 | 1 | 247 | 244 | 243 | 428 | 425 | 425 | 120 mm² |  | 0 | 13 | 44 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 13; Total Load B: 44; Total Load N: 0 | 44 | 0 | 32.618 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.512111, 56.864931 | 1040 | Pole (PMT) |  | 315 | 24/05/2026, 14:41 | 1 | 245 | 245 | 244 | 425 | 424 | 422 | 120 mm² |  | 89 | 36 | 45 | 32 | 185 mm² |  | 56 | 120 | 91 | 55 | [32 empty] | Total Load R: 145; Total Load Y: 156; Total Load B: 136; Total Load N: 87 | 156 | 136 | 36.4555 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.501564, 56.86238 | 2157 | Pole (PMT) |  | 315 | 24/05/2026, 14:34 | 1 | 245 | 247 | 246 | 426 | 427 | 426 | 185 mm² |  | 47 | 26 | 11 | 32 | 185 mm² |  | 12 | 33 | 11 | 0 | [32 empty] | Total Load R: 59; Total Load Y: 59; Total Load B: 22; Total Load N: 32 | 59 | 22 | 13.8201 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.501564, 56.86238 | 1039 | Pole (PMT) |  | 315 | 24/05/2026, 14:28 | 1 | 247 | 247 | 246 | 426 | 427 | 425 | 185 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 74 | 77 | 90 | 23 | [32 empty] | Total Load R: 74; Total Load Y: 77; Total Load B: 90; Total Load N: 23 | 90 | 74 | 21.0815 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.501564, 56.86238 | 1038 | Pole (PMT) |  | 315 | 24/05/2026, 14:21 | 1 | 247 | 247 | 246 | 437 | 438 | 439 | 185 mm² |  | 21 | 63 | 42 | 27 | 185 mm² |  | 107 | 114 | 92 | 26 | [32 empty] | Total Load R: 128; Total Load Y: 177; Total Load B: 134; Total Load N: 53 | 177 | 128 | 42.5309 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.501564, 56.86238 | 1995 | Pole (PMT) |  | 100 | 24/05/2026, 14:15 | 1 | 230 | 230 | 229 | 397 | 395 | 398 | 185 mm² |  | 10 | 52 | 43 | 30 | 185 mm² |  | 18 | 12 | 21 | 10 | [32 empty] | Total Load R: 28; Total Load Y: 64; Total Load B: 64; Total Load N: 40 | 64 | 28 | 44.0079 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.501564, 56.86238 | 1644 | Pole (PMT) |  | 100 | 24/05/2026, 14:07 | 1 | 247 | 246 | 244 | 428 | 424 | 426 | 120 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.50044, 56.856872 | 1889 | Ground (GMT) |  | 1000 | 24/05/2026, 13:58 | 1 | 233 | 234 | 234 | 401 | 404 | 407 | 185 mm² |  | 19 | 22 | 28 | 10 | 185 mm² |  | 0 | 14 | 16 | 12 | 185 mm² |  | 13 | 15 | 13 | 0 | [26 empty] | Total Load R: 32; Total Load Y: 51; Total Load B: 57; Total Load N: 22 | 57 | 32 | 3.9589 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.393625, 56.717511 | 1010 | Pole (PMT) |  | 100 | 23/05/2026, 16:33 | 1 | 234 | 234 | 236 | 390 | 395 | 399 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.466512, 56.796931 | 1009 | Pole (PMT) |  | 100 | 23/05/2026, 16:31 | 1 | 225 | 224 | 228 | 390 | 399 | 394 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.494735, 56.831695 | 1007 | Ground (GMT) |  | 500 | 23/05/2026, 16:01 | 1 | 226 | 228 | 227 | 393 | 391 | 397 | [6 empty] | 120 mm² |  | 70 | 28 | 128 | 83 | 120 mm² |  | 0 | 16 | 0 | 13 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 43 | 18 | 0 | 26 | 185 mm² |  | 70 | 80 | 71 | 0 | [8 empty] | Total Load R: 183; Total Load Y: 142; Total Load B: 199; Total Load N: 122 | 199 | 142 | 27.0917 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.490272, 56.826893 | 1003 | Pole (PMT) |  | 315 | 23/05/2026, 15:48 | 1 | 234 | 235 | 235 | 407 | 405 | 408 | 240 mm² |  | 0 | 0 | 16 | 0 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 0 | 0 | 0 | 0 | [26 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 16; Total Load N: 0 | 16 | 0 | 3.5807 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.490272, 56.826893 | 1002 | Pole (PMT) |  | 315 | 23/05/2026, 15:38 | 1 | 232 | 234 | 234 | 404 | 403 | 405 | 120 mm² |  | 34 | 68 | 49 | 44 | [38 empty] | Total Load R: 34; Total Load Y: 68; Total Load B: 49; Total Load N: 44 | 68 | 34 | 15.1057 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.487993, 56.827991 | 1005 | Pole (PMT) |  | 200 | 23/05/2026, 15:33 | 1 | 230 | 232 | 232 | 401 | 399 | 402 | 120 mm² |  | 0 | 26 | 0 | 19 | 120 mm² |  | 49 | 27 | 65 | 42 | [32 empty] | Total Load R: 49; Total Load Y: 53; Total Load B: 65; Total Load N: 61 | 65 | 49 | 22.573 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.487993, 56.827991 | 1004 | Pole (PMT) |  | 315 | 23/05/2026, 15:27 | 1 | 242 | 244 | 244 | 421 | 420 | 426 | 185 mm² |  | 179 | 127 | 194 | 65 | 70 mm² |  | 0 | 0 | 0 | 45 | [32 empty] | Total Load R: 179; Total Load Y: 127; Total Load B: 194; Total Load N: 110 | 194 | 127 | 44.9091 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.484966, 56.81935 | 2334 | Ground (GMT) |  | 1000 | 23/05/2026, 15:21 | 1 | 232 | 235 | 234 | 403 | 402 | 408 | 185 mm² |  | 71 | 43 | 48 | 29 | 185 mm² |  | 54 | 36 | 63 | 21 | 185 mm² |  | 66 | 64 | 115 | 33 | [26 empty] | Total Load R: 191; Total Load Y: 143; Total Load B: 226; Total Load N: 83 | 226 | 143 | 15.7752 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.484966, 56.81935 | 1872 | Ground (GMT) |  | 1000 | 23/05/2026, 15:13 | 1 | 233 | 236 | 235 | 406 | 404 | 410 | [12 empty] | 185 mm² |  | 53 | 22 | 43 | 21 | 185 mm² |  | 64 | 14 | 47 | 48 | 185 mm² |  | 100 | 59 | 83 | 32 | 185 mm² |  | 74 | 48 | 60 | 12 | [8 empty] | Total Load R: 291; Total Load Y: 143; Total Load B: 233; Total Load N: 113 | 291 | 143 | 20.4635 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.485603, 56.816834 | 1327 | Pole (PMT) |  | 315 | 23/05/2026, 15:03 | 1 | 223 | 226 | 226 | 390 | 388 | 390 | 185 mm² |  | 27 | 0 | 0 | 21 | 70 mm² |  | 12 | 0 | 0 | 12 | [32 empty] | Total Load R: 39; Total Load Y: 0; Total Load B: 0; Total Load N: 33 | 39 | 0 | 8.3633 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.477985, 56.798538 | 995 | Pole (PMT) |  | 315 | 23/05/2026, 14:56 | 1 | 230 | 232 | 232 | 400 | 400 | 402 | 120 mm² |  | 0 | 14 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 14; Total Load B: 0; Total Load N: 0 | 14 | 0 | 3.0792 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.477985, 56.798538 | 994 | Pole (PMT) |  | 100 | 23/05/2026, 14:46 | 1 | 225 | 227 | 228 | 390 | 394 | 394 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.477985, 56.798538 | 0 | Pole (PMT) |  | 315 | 23/05/2026, 14:38 | 1 | 229 | 230 | 231 | 398 | 397 | 401 | 240 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.467138, 56.79595 | 993 | Pole (PMT) |  | 100 | 23/05/2026, 14:31 | 1 | 221 | 239 | 243 | 418 | 416 | 419 | 120 mm² |  | 0 | 11 | 13 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 11; Total Load B: 13; Total Load N: 0 | 13 | 0 | 9.412 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN04 | 23.467138, 56.79595 | 00 | Pole (PMT) |  | 100 | 23/05/2026, 14:24 | 1 | 246 | 246 | 248 | 423 | 428 | 426 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.467138, 56.79595 | 04787 | Pole (PMT) |  | 100 | 23/05/2026, 14:18 | 1 | 245 | 245 | 248 | 423 | 429 | 426 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | AL-NUJAYD | K_LN04 | 23.465054, 56.795512 | 992 | Ground (GMT) |  | 1000 | 23/05/2026, 14:08 | 1 | 240 | 240 | 243 | 413 | 420 | 418 | 120 mm² | [5 empty] | 185 mm² |  | 63 | 60 | 34 | 35 | 120 mm² |  | 80 | 129 | 65 | 43 | 120 mm² |  | 192 | 125 | 123 | 49 | 120 mm² |  | 231 | 116 | 128 | 92 | 120 mm² |  | 230 | 117 | 129 | 94 | [8 empty] | Total Load R: 796; Total Load Y: 547; Total Load B: 479; Total Load N: 313 | 796 | 479 | 56.9408 | OK - No Upgrade | Need to Balance
Hijermat | AL-NUJAYD | K_LN4 | 23.480926, 57.038498 | 1031 | Ground (GMT) |  | 500 | 21/05/2026, 08:30 | 1 | 240 | 243 | 233 | 423 | 421 | 422 | 185 mm² |  | 184 | 142 | 114 | 51 | 185 mm² |  | 37 | 36 | 31 | 29 | 185 mm² | [31 empty] | Total Load R: 221; Total Load Y: 178; Total Load B: 145; Total Load N: 80 | 221 | 145 | 32.3835 | OK - No Upgrade | Need to Balance

## KAHANAT
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Hijermat | KAHANAT | K_LN3 | 23.704353, 56.795154 | 1010 | Ground (GMT) |  | 500 | 26/05/2026, 15:37 | 1 | 215 | 219 | 216 | 376 | 372 | 378 | [6 empty] | 120 mm² |  | 0 | 10 | 0 | 11 | [32 empty] | Total Load R: 0; Total Load Y: 10; Total Load B: 0; Total Load N: 11 | 10 | 0 | 1.3025 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.709008, 56.771666 | 1167 | Pole (PMT) |  | 315 | 26/05/2026, 14:56 | 1 | 213 | 216 | 216 | 378 | 372 | 375 | 185 mm² |  | 57 | 38 | 34 | 20 | 120 mm² |  | 64 | 69 | 18 | 50 | [32 empty] | Total Load R: 121; Total Load Y: 107; Total Load B: 52; Total Load N: 70 | 121 | 52 | 25.1494 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.715073, 56.762166 | 1162 | Pole (PMT) |  | 100 | 26/05/2026, 14:42 | 1 | 212 | 215 | 214 | 369 | 366 | 373 | [6 empty] | 120 mm² |  | 58 | 68 | 76 | 17 | [32 empty] | Total Load R: 58; Total Load Y: 68; Total Load B: 76; Total Load N: 17 | 76 | 58 | 48.5736 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.719028, 56.762924 | 1164 | Pole (PMT) |  | 100 | 26/05/2026, 14:34 | 1 | 217 | 214 | 219 | 374 | 372 | 379 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN3 | 23.716707, 56.763466 | 1163 | Pole (PMT) |  | 100 | 26/05/2026, 14:32 | 1 | 214 | 219 | 217 | 374 | 372 | 379 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN1 | 23.716444, 56.763265 | 867 | Pole (PMT) |  | 100 | 26/05/2026, 14:31 | 1 | 214 | 219 | 217 | 374 | 372 | 379 | 185 mm² |  | 28 | 0 | 0 | 21 | [38 empty] | Total Load R: 28; Total Load Y: 0; Total Load B: 0; Total Load N: 21 | 28 | 0 | 18.138 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.70195, 56.751904 | 1161 | Pole (PMT) |  | 200 | 26/05/2026, 14:20 | 1 | 214 | 218 | 218 | 373 | 373 | 379 | 185 mm² |  | 62 | 34 | 83 | 45 | 120 mm² |  | 60 | 67 | 20 | 43 | [32 empty] | Total Load R: 122; Total Load Y: 101; Total Load B: 103; Total Load N: 88 | 122 | 101 | 39.4094 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.694289, 56.755262 | 2227 | Pole (PMT) |  | 100 | 26/05/2026, 14:15 | 1 | 229 | 227 | 226 | 378 | 378 | 375 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN3 | 23.688352, 56.755606 | 1160 | Pole (PMT) |  | 315 | 26/05/2026, 14:10 | 1 | 214 | 219 | 219 | 373 | 376 | 381 | 120 mm² |  | 172 | 46 | 47 | 120 | [38 empty] | Total Load R: 172; Total Load Y: 46; Total Load B: 47; Total Load N: 120 | 172 | 46 | 35.2767 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.683931, 56.761754 | 1159 | Pole (PMT) |  | 315 | 26/05/2026, 14:04 | 1 | 218 | 221 | 219 | 378 | 376 | 382 | 120 mm² |  | 37 | 38 | 115 | 66 | [38 empty] | Total Load R: 37; Total Load Y: 38; Total Load B: 115; Total Load N: 66 | 115 | 37 | 23.9023 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.680853, 56.763108 | 1158 | Pole (PMT) |  | 100 | 26/05/2026, 13:59 | 1 | 223 | 225 | 223 | 410 | 411 | 410 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN3 | 23.676777, 56.766725 | 1157 | Pole (PMT) |  | 100 | 26/05/2026, 13:56 | 1 | 222 | 223 | 224 | 389 | 387 | 389 | 120 mm² | [5 empty] | 120 mm² |  | 0 | 0 | 18 | 19 | [32 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 18; Total Load N: 19 | 18 | 0 | 12.1278 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.67856, 56.774399 | 1156 | Pole (PMT) |  | 100 | 26/05/2026, 13:49 | 1 | 223 | 224 | 222 | 381 | 386 | 381 | 120 mm² |  | 0 | 24 | 35 | 26 | [38 empty] | Total Load R: 0; Total Load Y: 24; Total Load B: 35; Total Load N: 26 | 35 | 0 | 23.0969 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.669618, 56.778035 | 4645 | Pole (PMT) |  | 100 | 26/05/2026, 13:44 | 1 | 240 | 241 | 240 | 400 | 402 | 401 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN3 | 23.669655, 56.778017 | 1155 | Pole (PMT) |  | 315 | 26/05/2026, 13:40 | 1 | 226 | 227 | 226 | 396 | 389 | 393 | 120 mm² |  | 150 | 59 | 82 | 68 | [38 empty] | Total Load R: 150; Total Load Y: 59; Total Load B: 82; Total Load N: 68 | 150 | 59 | 32.6615 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.650701, 56.797719 | 1154 | Pole (PMT) |  | 315 | 26/05/2026, 13:30 | 1 | 225 | 227 | 228 | 390 | 392 | 391 |  |  | 62 | 99 | 37 | 55 | 120 mm² |  | 70 | 58 | 42 | 23 | [32 empty] | Total Load R: 132; Total Load Y: 157; Total Load B: 79; Total Load N: 78 | 157 | 79 | 33.6678 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.648862, 56.79917 | 1513 | Pole (PMT) |  | 100 | 26/05/2026, 13:25 | 1 | 227 | 228 | 229 | 394 | 396 | 397 | 120 mm² |  | 16 | 35 | 26 | 17 | 120 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 16; Total Load Y: 35; Total Load B: 26; Total Load N: 17 | 35 | 16 | 23.885 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.642976, 56.803126 | 1863 | Pole (PMT) |  | 200 | 26/05/2026, 13:21 | 1 | 227 | 230 | 231 | 394 | 396 | 401 | 185 mm² |  | 46 | 23 | 10 | 37 | [38 empty] | Total Load R: 46; Total Load Y: 23; Total Load B: 10; Total Load N: 37 | 46 | 10 | 15.6958 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.638793, 56.803854 | 4426 | Pole (PMT) |  | 100 | 26/05/2026, 13:15 | 1 | 229 | 232 | 233 | 398 | 400 | 402 | 185 mm² |  | 0 | 0 | 0 | 0 |  |  | 34 | 0 | 0 | 30 | [32 empty] | Total Load R: 34; Total Load Y: 0; Total Load B: 0; Total Load N: 30 | 34 | 0 | 23.4381 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.64112, 56.803781 | 1653 | Pole (PMT) |  | 315 | 26/05/2026, 13:01 | 1 | 230 | 233 | 233 | 366 | 401 | 404 | 185 mm² |  | 29 | 27 | 34 | 11 | [38 empty] | Total Load R: 29; Total Load Y: 27; Total Load B: 34; Total Load N: 11 | 34 | 27 | 6.8424 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.636239, 56.802786 | 1153 | Pole (PMT) |  | 100 | 26/05/2026, 12:56 | 1 | 241 | 240 | 241 | 420 | 421 | 420 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN3 | 23.636361, 56.804439 | 2046 | Ground (GMT) |  | 500 | 26/05/2026, 12:53 | 1 | 231 | 234 | 233 | 400 | 405 | 404 | [6 empty] | 185 mm² |  | 49 | 16 | 75 | 47 | 185 mm² |  | 52 | 62 | 37 | 109 | 185 mm² |  | 42 | 55 | 59 | 30 | 185 mm² |  | 62 | 49 | 51 | 23 | 185 mm² |  | 41 | 88 | 105 | 44 | [8 empty] | Total Load R: 246; Total Load Y: 270; Total Load B: 327; Total Load N: 253 | 327 | 246 | 45.3104 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.631391, 56.806943 | 1545 | Pole (PMT) |  | 100 | 26/05/2026, 12:41 | 1 | 235 | 235 | 235 | 407 | 403 | 409 | [6 empty] | 120 mm² |  | 0 | 18 | 27 | 23 | [32 empty] | Total Load R: 0; Total Load Y: 18; Total Load B: 27; Total Load N: 23 | 27 | 0 | 19.0335 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.632231, 56.810287 | 949 | Pole (PMT) |  | 315 | 26/05/2026, 12:37 | 1 | 246 | 247 | 248 | 427 | 429 | 424 | 120 mm² |  | 71 | 69 | 38 | 32 | 120 mm² |  | 72 | 22 | 74 | 69 | [32 empty] | Total Load R: 143; Total Load Y: 91; Total Load B: 112; Total Load N: 101 | 143 | 91 | 33.5748 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.628825, 56.801291 | 1927 | Pole (PMT) |  | 315 | 25/05/2026, 15:23 | 1 | 228 | 229 | 228 | 398 | 396 | 397 | 185 mm² |  | 8 | 1 | 9 | 6 | 185 mm² |  | 0 | 8 | 2 | 2 | [32 empty] | Total Load R: 8; Total Load Y: 9; Total Load B: 11; Total Load N: 8 | 11 | 8 | 2.4073 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.627779, 56.798788 | 948 | Pole (PMT) |  | 315 | 25/05/2026, 15:18 | 1 | 227 | 228 | 227 | 395 | 394 | 394 | 120 mm² |  | 78 | 58 | 114 | 38 | 120 mm² |  | 11 | 11 | 14 | 4 | [32 empty] | Total Load R: 89; Total Load Y: 69; Total Load B: 128; Total Load N: 42 | 128 | 69 | 27.8008 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.624611, 56.810204 | 947 | Pole (PMT) |  | 200 | 25/05/2026, 15:10 | 1 | 226 | 227 | 226 | 393 | 392 | 392 | 120 mm² |  | 82 | 42 | 52 | 44 | 120 mm² |  | 23 | 31 | 19 | 10 | [32 empty] | Total Load R: 105; Total Load Y: 73; Total Load B: 71; Total Load N: 54 | 105 | 71 | 35.7365 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.624834, 56.810489 | 946 | Pole (PMT) |  | 315 | 25/05/2026, 15:05 | 1 | 228 | 229 | 228 | 395 | 395 | 396 | 120 mm² | [5 empty] | 120 mm² |  | 117 | 111 | 100 | 25 | [32 empty] | Total Load R: 117; Total Load Y: 111; Total Load B: 100; Total Load N: 25 | 117 | 100 | 25.4117 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN3 | 23.595666, 56.799388 | 945 | Pole (PMT) |  | 100 | 25/05/2026, 14:58 | 1 | 212 | 245 | 244 | 423 | 421 | 425 | 120 mm² |  | 57 | 16 | 18 | 28 | 120 mm² |  | 5 | 0 | 9 | 5 | [32 empty] | Total Load R: 62; Total Load Y: 16; Total Load B: 27; Total Load N: 33 | 62 | 16 | 45.4248 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.580841, 56.80362 | 944 | Pole (PMT) |  | 200 | 25/05/2026, 14:52 | 1 | 232 | 233 | 233 | 404 | 404 | 402 | 185 mm² |  | 67 | 13 | 44 | 36 | 120 mm² |  | 72 | 20 | 41 | 19 | [32 empty] | Total Load R: 139; Total Load Y: 33; Total Load B: 85; Total Load N: 55 | 139 | 33 | 48.6325 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.581216, 56.791283 | 943 | Pole (PMT) |  | 315 | 25/05/2026, 14:44 | 1 | 233 | 234 | 234 | 404 | 406 | 405 | 120 mm² |  | 119 | 76 | 126 | 35 | [38 empty] | Total Load R: 119; Total Load Y: 76; Total Load B: 126; Total Load N: 35 | 126 | 76 | 27.9899 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.558004, 56.794865 | 1485 | Pole (PMT) |  | 100 | 25/05/2026, 14:39 | 1 | 233 | 232 | 231 | 408 | 406 | 409 | 120 mm² |  | 9 | 7 | 0 | 2 | [38 empty] | Total Load R: 9; Total Load Y: 7; Total Load B: 0; Total Load N: 2 | 9 | 0 | 6.3601 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.554009, 56.798819 | 1019 | Pole (PMT) |  | 100 | 25/05/2026, 14:36 | 1 | 236 | 236 | 236 | 409 | 408 | 409 | 120 mm² |  | 23 | 23 | 29 | 5 | 120 mm² |  | 25 | 15 | 21 | 15 | [32 empty] | Total Load R: 48; Total Load Y: 38; Total Load B: 50; Total Load N: 20 | 50 | 38 | 35.4204 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.551932, 56.80363 | 1018 | Pole (PMT) |  | 100 | 25/05/2026, 14:31 | 1 | 237 | 235 | 238 | 411 | 415 | 413 | 120 mm² |  | 12 | 0 | 0 | 9 | [38 empty] | Total Load R: 12; Total Load Y: 0; Total Load B: 0; Total Load N: 9 | 12 | 0 | 8.5425 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.54732, 56.817511 | 4406 | Pole (PMT) |  | 100 | 25/05/2026, 14:25 | 1 | 227 | 226 | 227 | 395 | 391 | 391 | [6 empty] | 185 mm² |  | 2 | 8 | 0 | 0 | [32 empty] | Total Load R: 2; Total Load Y: 8; Total Load B: 0; Total Load N: 0 | 8 | 0 | 5.4733 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.551217, 56.822527 | 1017 | Pole (PMT) |  | 315 | 25/05/2026, 14:18 | 1 | 236 | 237 | 237 | 413 | 410 | 413 | 120 mm² |  | 115 | 40 | 20 | 80 | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 115; Total Load Y: 40; Total Load B: 20; Total Load N: 80 | 115 | 20 | 26.1155 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.541563, 56.824032 | 4428 | Pole (PMT) |  | 100 | 25/05/2026, 14:13 | 1 | 237 | 237 | 237 | 413 | 410 | 410 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN1 | 23.554217, 56.849939 | 1015 | Pole (PMT) |  | 100 | 25/05/2026, 14:00 | 1 | 240 | 241 | 240 | 429 | 428 | 430 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN1 | 23.555819, 56.84894 | 1016 | Pole (PMT) |  | 100 | 25/05/2026, 13:55 | 1 | 249 | 247 | 249 | 431 | 431 | 431 | [6 empty] | 120 mm² |  | 10 | 24 | 14 | 15 | [32 empty] | Total Load R: 10; Total Load Y: 24; Total Load B: 14; Total Load N: 15 | 24 | 10 | 17.9163 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.538696, 56.83843 | 4582 | Pole (PMT) |  | 100 | 25/05/2026, 13:45 | 1 | 237 | 238 | 240 | 410 | 409 | 408 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN1 | 23.534941, 56.834887 | 1014 | Pole (PMT) |  | 100 | 25/05/2026, 13:39 | 1 | 236 | 235 | 236 | 412 | 413 | 411 | 120 mm² |  | 44 | 64 | 26 | 27 | [38 empty] | Total Load R: 44; Total Load Y: 64; Total Load B: 26; Total Load N: 27 | 64 | 26 | 45.6707 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.530983, 56.835035 | 4355 | Pole (PMT) |  | 50 | 25/05/2026, 13:36 | 1 | 241 | 240 | 239 | 417 | 410 | 418 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN1 | 23.523148, 56.842025 | 1013 | Pole (PMT) |  | 100 | 25/05/2026, 13:32 | 1 | 241 | 239 | 240 | 418 | 417 | 416 | 120 mm² |  | 5 | 7 | 13 | 10 | [38 empty] | Total Load R: 5; Total Load Y: 7; Total Load B: 13; Total Load N: 10 | 13 | 5 | 9.412 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.525381, 56.843145 | 2332 | Pole (PMT) |  | 100 | 25/05/2026, 13:27 | 1 | 240 | 240 | 241 | 417 | 417 | 416 | 120 mm² |  | 20 | 8 | 12 | 12 | [38 empty] | Total Load R: 20; Total Load Y: 8; Total Load B: 12; Total Load N: 12 | 20 | 8 | 14.4453 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.514874, 56.842648 | 1012 | Pole (PMT) |  | 100 | 25/05/2026, 13:20 | 1 | 228 | 230 | 229 | 400 | 396 | 396 | 120 mm² |  | 16 | 10 | 23 | 12 | 120 mm² |  | 22 | 10 | 23 | 16 | [32 empty] | Total Load R: 38; Total Load Y: 20; Total Load B: 46; Total Load N: 28 | 46 | 20 | 31.8697 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.511803, 56.846373 | 2086 | Pole (PMT) |  | 100 | 25/05/2026, 13:14 | 1 | 241 | 243 | 242 | 422 | 420 | 424 | 185 mm² |  | 13 | 8 | 17 | 10 | [38 empty] | Total Load R: 13; Total Load Y: 8; Total Load B: 17; Total Load N: 10 | 17 | 8 | 12.4257 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.507663, 56.841495 | 1799 | Pole (PMT) |  | 100 | 25/05/2026, 13:08 | 1 | 254 | 253 | 251 | 440 | 443 | 449 | 120 mm² |  | 28 | 29 | 56 | 28 | [38 empty] | Total Load R: 28; Total Load Y: 29; Total Load B: 56; Total Load N: 28 | 56 | 28 | 42.6777 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.504801, 56.8472 | 1011 | Pole (PMT) |  | 100 | 25/05/2026, 13:01 | 1 | 237 | 238 | 238 | 414 | 414 | 413 | 120 mm² |  | 6 | 15 | 6 | 9 | 120 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 6; Total Load Y: 15; Total Load B: 6; Total Load N: 9 | 15 | 6 | 10.756 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN3 | 23.558002, 56.780938 | 45 | Ground (GMT) |  | 1000 | 24/05/2026, 15:40 | 1 | 235 | 235 | 235 | 409 | 407 | 407 | [12 empty] | 185 mm² |  | 150 | 78 | 94 | 75 | 185 mm² |  | 216 | 132 | 119 | 75 | 185 mm² |  | 0 | 0 | 0 | 0 | [14 empty] | Total Load R: 366; Total Load Y: 210; Total Load B: 213; Total Load N: 150 | 366 | 210 | 25.9278 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.561234, 56.785092 | 942 | Pole (PMT) |  | 200 | 24/05/2026, 15:31 | 1 | 234 | 234 | 234 | 407 | 406 | 406 | 120 mm² | [5 empty] | 120 mm² |  | 79 | 66 | 99 | 34 | [32 empty] | Total Load R: 79; Total Load Y: 66; Total Load B: 99; Total Load N: 34 | 99 | 66 | 34.8948 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.561262, 56.783789 | 4423 | Pole (PMT) |  | 100 | 24/05/2026, 15:28 | 1 | 237 | 236 | 236 | 410 | 409 | 408 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN1 | 23.554779, 56.782366 | 941 | Pole (PMT) |  | 315 | 24/05/2026, 15:22 | 1 | 236 | 235 | 235 | 408 | 408 | 408 | 120 mm² |  | 10 | 20 | 11 | 13 | 120 mm² |  | 38 | 36 | 78 | 29 | [32 empty] | Total Load R: 48; Total Load Y: 56; Total Load B: 89; Total Load N: 42 | 89 | 48 | 19.9664 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.555402, 56.781685 | 939 | Pole (PMT) |  | 315 | 24/05/2026, 15:19 | 1 | 225 | 227 | 230 | 390 | 400 | 399 | 120 mm² |  | 34 | 46 | 25 | 19 | [38 empty] | Total Load R: 34; Total Load Y: 46; Total Load B: 25; Total Load N: 19 | 46 | 25 | 9.8644 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.553636, 56.780435 | 938 | Ground (GMT) |  | 1000 | 24/05/2026, 15:15 | 1 | 242 | 241 | 241 | 418 | 418 | 417 | [12 empty] | 120 mm² |  | 36 | 26 | 33 | 9 | 120 mm² |  | 46 | 52 | 64 | 10 | 120 mm² |  | 127 | 114 | 72 | 41 | 120 mm² |  | 35 | 64 | 29 | 31 | 120 mm² |  | 53 | 61 | 42 | 31 | 120 mm² |  | 56 | 104 | 134 | 49 | 353 | 421 | 374 | 171 | 421 | 353 | 30.4803 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.551333, 56.780924 | 937 | Pole (PMT) |  | 315 | 24/05/2026, 15:10 | 1 | 235 | 234 | 237 | 408 | 409 | 402 | 120 mm² |  | 26 | 34 | 35 | 8 | 120 mm² |  | 117 | 85 | 55 | 40 | [32 empty] | Total Load R: 143; Total Load Y: 119; Total Load B: 90; Total Load N: 48 | 143 | 90 | 32.0809 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.549353, 56.778659 | 4687 | Ground (GMT) |  | 1000 | 24/05/2026, 15:06 | 1 | 236 | 236 | 236 | 411 | 410 | 412 | 185 mm² |  | 182 | 203 | 223 | 41 | 185 mm² |  | 42 | 15 | 49 | 31 | 185 mm² |  | 54 | 35 | 67 | 35 | [26 empty] | Total Load R: 278; Total Load Y: 253; Total Load B: 339; Total Load N: 107 | 339 | 253 | 24.1325 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.547669, 56.775566 | 935 | Pole (PMT) |  | 315 | 24/05/2026, 14:58 | 1 | 232 | 234 | 235 | 403 | 405 | 402 | 185 mm² |  | 175 | 122 | 137 | 46 | 185 mm² |  | 161 | 114 | 80 | 75 | [32 empty] | Total Load R: 336; Total Load Y: 236; Total Load B: 217; Total Load N: 121 | 336 | 217 | 74.4551 | Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.547625, 56.775096 | 934 | Pole (PMT) |  | 200 | 24/05/2026, 14:55 | 1 | 233 | 232 | 235 | 403 | 407 | 404 | 120 mm² |  | 98 | 96 | 50 | 47 | 120 mm² |  | 80 | 82 | 60 | 35 | [32 empty] | Total Load R: 178; Total Load Y: 178; Total Load B: 110; Total Load N: 82 | 178 | 110 | 62.1235 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN1 | 23.546846, 56.772395 | 933 | Pole (PMT) |  | 315 | 24/05/2026, 14:51 | 1 | 238 | 238 | 231 | 409 | 412 | 411 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 97 | 40 | 80 | 58 | [32 empty] | Total Load R: 97; Total Load Y: 40; Total Load B: 80; Total Load N: 58 | 97 | 40 | 21.8145 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.550411, 56.772407 | 4326 | Pole (PMT) |  | 100 | 24/05/2026, 14:46 | 1 | 241 | 240 | 242 | 420 | 421 | 429 | 185 mm² |  | 7 | 6 | 5 | 1 | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 7; Total Load Y: 6; Total Load B: 5; Total Load N: 1 | 7 | 5 | 5.0922 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.547379, 56.77145 | 1733 | Pole (PMT) |  | 100 | 24/05/2026, 14:42 | 1 | 242 | 241 | 241 | 420 | 418 | 420 | 120 mm² | [5 empty] | 120 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN2 | 23.535058, 56.753144 | 2139 | Pole (PMT) |  | 315 | 24/05/2026, 14:36 | 1 | 241 | 241 | 240 | 418 | 419 | 416 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 7 | 0 | [32 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 7; Total Load N: 0 | 7 | 0 | 1.6089 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.536252, 56.756291 | 2024 | Pole (PMT) |  | 315 | 24/05/2026, 14:31 | 1 | 241 | 240 | 240 | 414 | 417 | 417 | 185 mm² |  | 16 | 24 | 56 | 30 | 185 mm² |  | 60 | 62 | 25 | 29 | [32 empty] | Total Load R: 76; Total Load Y: 86; Total Load B: 81; Total Load N: 59 | 86 | 76 | 19.5771 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN2 | 23.537734, 56.757799 | 4732 | Ground (GMT) |  | 500 | 24/05/2026, 14:26 | 1 | 240 | 240 | 241 | 417 | 415 | 415 | 185 mm² |  | 112 | 77 | 72 | 27 | 185 mm² |  | 32 | 48 | 12 | 18 | [32 empty] | Total Load R: 144; Total Load Y: 125; Total Load B: 84; Total Load N: 45 | 144 | 84 | 20.8012 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.541659, 56.754939 | 1172 | Pole (PMT) |  | 315 | 24/05/2026, 14:19 | 1 | 237 | 238 | 239 | 414 | 412 | 412 | 185 mm² |  | 104 | 78 | 40 | 55 | 185 mm² |  | 225 | 151 | 50 | 45 | [32 empty] | Total Load R: 329; Total Load Y: 229; Total Load B: 90; Total Load N: 100 | 329 | 90 | 74.8939 | Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.541731, 56.761641 | 1170 | Ground (GMT) |  | 1000 | 24/05/2026, 14:13 | 1 | 241 | 241 | 241 | 420 | 418 | 417 | 185 mm² |  | 17 | 43 | 25 | 21 | 185 mm² |  | 230 | 98 | 105 | 91 |  |  | 83 | 81 | 53 | 27 |  |  | 65 | 53 | 49 | 26 |  |  | 25 | 63 | 32 | 20 | [14 empty] | Total Load R: 420; Total Load Y: 338; Total Load B: 264; Total Load N: 185 | 420 | 264 | 30.5534 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.541208, 56.761558 | 1171 | Ground (GMT) |  | 500 | 24/05/2026, 14:05 | 1 | 232 | 231 | 233 | 403 | 403 | 402 | 185 mm² |  | 25 | 23 | 25 | 18 | [38 empty] | Total Load R: 25; Total Load Y: 23; Total Load B: 25; Total Load N: 18 | 25 | 23 | 3.4901 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN2 | 23.542132, 56.767117 | 1169 | Pole (PMT) |  | 315 | 24/05/2026, 13:59 | 1 | 232 | 229 | 232 | 402 | 401 | 403 | 120 mm² |  | 11 | 11 | 15 | 0 | 120 mm² |  | 13 | 59 | 20 | 33 | [32 empty] | Total Load R: 24; Total Load Y: 70; Total Load B: 35; Total Load N: 33 | 70 | 24 | 15.473 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.537768, 56.769729 | 1070 | Pole (PMT) |  | 100 | 24/05/2026, 13:52 | 1 | 244 | 244 | 245 | 426 | 426 | 424 | 120 mm² | [7 empty] | 12 | 12 | 11 | 0 | [32 empty] | Total Load R: 12; Total Load Y: 12; Total Load B: 11; Total Load N: 0 | 12 | 11 | 8.8542 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN2 | 23.534544, 56.762356 | 1174 | Pole (PMT) |  | 100 | 24/05/2026, 13:43 | 1 | 245 | 246 | 246 | 426 | 429 | 426 | 120 mm² |  | 24 | 10 | 8 | 18 | 120 mm² |  | 8 | 5 | 10 | 7 | [32 empty] | Total Load R: 32; Total Load Y: 15; Total Load B: 18; Total Load N: 25 | 32 | 15 | 23.6113 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.542801, 56.740032 | 1176 | Pole (PMT) |  | 100 | 23/05/2026, 15:43 | 1 | 235 | 236 | 235 | 408 | 409 | 408 | 120 mm² |  | 52 | 35 | 34 | 17 | [38 empty] | Total Load R: 52; Total Load Y: 35; Total Load B: 34; Total Load N: 17 | 52 | 34 | 36.7472 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.541778, 56.741336 | 2171 | Pole (PMT) |  | 315 | 23/05/2026, 15:35 | 1 | 239 | 237 | 237 | 412 | 418 | 410 | 120 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 8 | 5 | 18 | 9 | [32 empty] | Total Load R: 8; Total Load Y: 5; Total Load B: 18; Total Load N: 9 | 18 | 5 | 4.0777 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.542366, 56.739375 | 1173 | Pole (PMT) |  | 100 | 23/05/2026, 15:30 | 1 | 237 | 236 | 236 | 412 | 409 | 404 | [6 empty] | 120 mm² |  | 23 | 47 | 32 | 23 | [32 empty] | Total Load R: 23; Total Load Y: 47; Total Load B: 32; Total Load N: 23 | 47 | 23 | 33.5394 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.524329, 56.760567 | 1175 | Pole (PMT) |  | 100 | 23/05/2026, 15:24 | 1 | 238 | 237 | 239 | 414 | 413 | 414 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN2 | 23.515238, 56.764417 | 2216 | Pole (PMT) |  | 315 | 23/05/2026, 15:11 | 1 | 238 | 239 | 238 | 413 | 414 | 413 | 185 mm² |  | 12 | 13 | 9 | 4 | [38 empty] | Total Load R: 12; Total Load Y: 13; Total Load B: 9; Total Load N: 4 | 13 | 9 | 2.9522 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.507867, 56.76516 | 1509 | Pole (PMT) |  | 100 | 23/05/2026, 15:07 | 1 | 237 | 238 | 238 | 413 | 411 | 412 | [6 empty] | 120 mm² |  | 32 | 12 | 10 | 20 | [32 empty] | Total Load R: 32; Total Load Y: 12; Total Load B: 10; Total Load N: 20 | 32 | 10 | 22.8908 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.510851, 56.751188 | 1724 | Pole (PMT) |  | 100 | 23/05/2026, 14:57 | 1 | 241 | 241 | 240 | 416 | 414 | 415 | 120 mm² |  | 6 | 5 | 8 | 4 | [38 empty] | Total Load R: 6; Total Load Y: 5; Total Load B: 8; Total Load N: 4 | 8 | 5 | 5.7643 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.499607, 56.746235 | 4374 | Pole (PMT) |  | 315 | 23/05/2026, 14:46 | 1 | 240 | 241 | 241 | 415 | 416 | 415 | 185 mm² |  | 7 | 9 | 22 | 15 | 185 mm² |  | 8 | 4 | 4 | 0 | [32 empty] | Total Load R: 15; Total Load Y: 13; Total Load B: 26; Total Load N: 15 | 26 | 13 | 5.933 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.492498, 56.746122 | 1178 | Pole (PMT) |  | 315 | 23/05/2026, 14:42 | 1 | 240 | 240 | 238 | 414 | 414 | 417 | 120 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 15 | 18 | 75 | 65 | [32 empty] | Total Load R: 15; Total Load Y: 18; Total Load B: 75; Total Load N: 65 | 75 | 15 | 17.0731 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.494055, 56.762167 | 2251 | Pole (PMT) |  | 100 | 23/05/2026, 14:34 | 1 | 240 | 239 | 239 | 415 | 415 | 417 | 185 mm² |  | 8 | 15 | 11 | 12 | [38 empty] | Total Load R: 8; Total Load Y: 15; Total Load B: 11; Total Load N: 12 | 15 | 8 | 10.782 | OK - No Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.493949, 56.762073 | 2215 | Pole (PMT) |  | 100 |  | 1 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN2 | 23.486199, 56.712678 | 1890 | Pole (PMT) |  | 315 |  | 1 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN2 |  | 4546 | Pole (PMT) |  | 100 | 23/05/2026, 14:23 | 1 | 241 | 241 | 241 | 419 | 419 | 420 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | KAHANAT | K_LN2 |  | 1180 | Pole (PMT) |  | 100 | 23/05/2026, 14:13 | 1 | 237 | 237 | 234 | 407 | 408 | 409 | 120 mm² |  | 76 | 82 | 108 | 25 | [38 empty] | Total Load R: 76; Total Load Y: 82; Total Load B: 108; Total Load N: 25 | 108 | 76 | 76.134 | Upgrade | Need to Balance
Hijermat | KAHANAT | K_LN2 | 23.483609, 56.719051 | 1481 | Pole (PMT) |  | 100 | 23/05/2026, 13:57 | 1 | 242 | 242 | 240 | 419 | 420 | 416 |  |  | 69 | 129 | 60 | 63 | [38 empty] | Total Load R: 69; Total Load Y: 129; Total Load B: 60; Total Load N: 63 | 129 | 60 | 93.6191 | Upgrade | Need to Balance

## HUGERMAT
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Feeder 9 | [5 empty] | Feeder 10 | [5 empty] | Feeder 11 | [5 empty] | Feeder 12 | [5 empty] | Feeder 13 | [5 empty] | Feeder 14 | [5 empty] | Feeder 15 | [5 empty] | Feeder 16 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Hijermat | HUGERMAT | K_LN04 | 23.402288, 56.724812 | 972 | Pole (PMT) | 3 | 315 | 10/06/2026, 16:05 | 1 | 232 | 236 | 232 | 403 | 403 | 403 | 185 mm² |  | 119 | 66 | 110 | 36 | 185 mm² |  | 85 | 54 | 16 | 57 | [80 empty] | Total Load R: 204; Total Load Y: 120; Total Load B: 126; Total Load N: 93 | 204 | 120 | 45.2049 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN04 | 23.403142, 56.727629 | 1615 | Pole (PMT) | 3 | 315 | 10/06/2026, 16:00 | 1 | 236 | 237 | 237 | 411 | 411 | 409 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 267 | 217 | 141 | 123 | [80 empty] | Total Load R: 267; Total Load Y: 217; Total Load B: 141; Total Load N: 123 | 267 | 141 | 60.3397 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN04 | 23.405429, 56.732253 | 1832 | Ground (GMT) | 3 | 1000 | 10/06/2026, 15:56 | 1 | 239 | 239 | 238 | 414 | 413 | 412 | [6 empty] | 120 mm² |  | 0 | 0 | 11 | 10 | [6 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 84 | 61 | 113 | 52 | 185 mm² |  | 60 | 83 | 120 | 59 | 185 mm² |  | 62 | 61 | 58 | 10 | [50 empty] | Total Load R: 206; Total Load Y: 205; Total Load B: 302; Total Load N: 131 | 302 | 205 | 21.6555 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN04 | 23.410329, 56.730767 | 0873 | Ground (GMT) | 3 | 1000 | 10/06/2026, 15:48 | 1 | 238 | 239 | 238 | 415 | 413 | 412 | [24 empty] | 120 mm² |  | 17 | 41 | 40 | 23 | 120 mm² |  | 57 | 80 | 29 | 56 | 185 mm² |  | 48 | 15 | 25 | 19 | 185 mm² |  | 163 | 116 | 146 | 49 | [44 empty] | Total Load R: 285; Total Load Y: 252; Total Load B: 240; Total Load N: 147 | 285 | 240 | 20.4858 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN04 | 23.413126, 56.738671 | 978 | Pole (PMT) | 3 | 315 | 10/06/2026, 15:35 | 1 | 233 | 235 | 234 | 407 | 406 | 405 | 120 mm² |  | 40 | 13 | 16 | 27 | 120 mm² |  | 104 | 94 | 94 | 14 | 185 mm² |  | 165 | 107 | 138 | 0 | [74 empty] | Total Load R: 309; Total Load Y: 214; Total Load B: 248; Total Load N: 41 | 309 | 214 | 69.1517 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN04 | 23.413425, 56.729188 | 968 | Ground (GMT) | 3 | 2000 | 10/06/2026, 15:25 | 1 | 243 | 244 | 244 | 421 | 421 | 423 | 185 mm² |  | 111 | 93 | 90 | 47 | 185 mm² |  | 82 | 68 | 49 | 12 | 185 mm² |  | 63 | 163 | 147 | 67 | 185 mm² |  | 0 | 0 | 14 | 13 | 185 mm² |  | 152 | 126 | 168 | 37 | 185 mm² |  | 165 | 158 | 175 | 27 | [6 empty] | 185 mm² |  | 45 | 52 | 0 | 37 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 96 | 116 | 67 | 32 | [26 empty] | Total Load R: 714; Total Load Y: 776; Total Load B: 710; Total Load N: 272 | 776 | 710 | 28.2927 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN04 | 23.413298, 56.72919 | 2062 | Ground (GMT) | 3 | 500 | 10/06/2026, 17:00 | 1 | 241 | 240 | 240 | 418 | 416 | 417 | 185 mm² |  | 35 | 40 | 55 | 30 | [86 empty] | Total Load R: 35; Total Load Y: 40; Total Load B: 55; Total Load N: 30 | 55 | 35 | 7.964 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN04 | 23.422437, 56.727213 | 967 | Pole (PMT) | 3 | 315 | 10/06/2026, 15:12 | 1 | 239 | 239 | 237 | 415 | 411 | 412 | 120 mm² |  | 127 | 100 | 137 | 35 | 120 mm² |  | 62 | 156 | 155 | 81 | [80 empty] | Total Load R: 189; Total Load Y: 256; Total Load B: 292; Total Load N: 116 | 292 | 189 | 66.6317 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN04 | 23.424905, 56.726891 | 1967 | Pole (PMT) | 3 | 315 | 10/06/2026, 15:06 | 1 | 243 | 245 | 245 | 421 | 424 | 423 | 185 mm² |  | 49 | 58 | 34 | 27 | 185 mm² |  | 144 | 52 | 75 | 75 | [80 empty] | Total Load R: 193; Total Load Y: 110; Total Load B: 109; Total Load N: 102 | 193 | 109 | 44.6776 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN04 | 23.423351, 56.724885 | 963 | Pole (PMT) | 3 | 315 | 10/06/2026, 15:02 | 1 | 245 | 247 | 247 | 426 | 427 | 425 | 120 mm² |  | 147 | 96 | 148 | 54 | 120 mm² |  | 52 | 35 | 20 | 37 | [80 empty] | Total Load R: 199; Total Load Y: 131; Total Load B: 168; Total Load N: 91 | 199 | 131 | 46.6136 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN04 | 23.413551, 56.726163 | 966 | Pole (PMT) | 3 | 315 | 10/06/2026, 14:54 | 1 | 239 | 239 | 238 | 414 | 413 | 414 | 120 mm² |  | 159 | 193 | 108 | 65 | 120 mm² |  | 114 | 112 | 175 | 52 | [80 empty] | Total Load R: 273; Total Load Y: 305; Total Load B: 283; Total Load N: 117 | 305 | 273 | 69.4305 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN04 | 23.422946, 56.721703 | 965 | Pole (PMT) | 3 | 200 | 10/06/2026, 14:49 | 1 | 244 | 245 | 244 | 425 | 424 | 423 | 120 mm² |  | 15 | 0 | 26 | 17 | 120 mm² |  | 105 | 57 | 63 | 47 | [80 empty] | Total Load R: 120; Total Load Y: 57; Total Load B: 89; Total Load N: 64 | 120 | 57 | 44.1673 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN04 | 23.422943, 56.721698 | 964 | Pole (PMT) | 3 | 315 | 10/06/2026, 14:46 | 1 | 241 | 241 | 240 | 419 | 417 | 415 | 120 mm² |  | 0 | 14 | 20 | 14 | 240 mm² |  | 12 | 34 | 11 | 24 | [80 empty] | Total Load R: 12; Total Load Y: 48; Total Load B: 31; Total Load N: 38 | 48 | 12 | 11.0587 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN04 | 23.425847, 56.711055 | 961 | Pole (PMT) | 3 | 200 | 10/06/2026, 14:40 | 1 | 246 | 245 | 245 | 427 | 424 | 425 | 120 mm² |  | 92 | 84 | 121 | 33 | 120 mm² |  | 0 | 35 | 24 | 22 | [80 empty] | Total Load R: 92; Total Load Y: 119; Total Load B: 145; Total Load N: 55 | 145 | 92 | 53.62 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN04 | 23.424261, 56.716002 | 960 | Pole (PMT) | 3 | 200 | 10/06/2026, 14:36 | 1 | 247 | 246 | 247 | 428 | 427 | 427 | 120 mm² |  | 41 | 82 | 58 | 37 | 120 mm² |  | 61 | 31 | 51 | 17 | [80 empty] | Total Load R: 102; Total Load Y: 113; Total Load B: 109; Total Load N: 54 | 113 | 102 | 41.8845 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN04 | 23.424028, 56.720763 | 1389 | Pole (PMT) | 3 | 100 | 10/06/2026, 14:32 | 1 | 254 | 253 | 253 | 440 | 439 | 440 | 185 mm² |  | 14 | 34 | 27 | 17 | [86 empty] | Total Load R: 14; Total Load Y: 34; Total Load B: 27; Total Load N: 17 | 34 | 14 | 25.9115 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN04 | 23.423698, 56.723812 | 962 | Ground (GMT) | 3 | 1000 | 10/06/2026, 14:27 | 1 | 249 | 249 | 248 | 432 | 431 | 432 | [6 empty] | 185 mm² |  | 77 | 84 | 128 | 47 | 185 mm² |  | 112 | 38 | 110 | 38 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 13 | 20 | 81 | 38 | 120 mm² |  | 0 | 32 | 48 | 46 | 185 mm² |  | 70 | 57 | 95 | 33 | 120 mm² |  | 113 | 72 | 85 | 35 | [44 empty] | Total Load R: 385; Total Load Y: 303; Total Load B: 547; Total Load N: 237 | 547 | 303 | 40.9291 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN04 | 23.426341, 56.725262 | 4248 | Ground (GMT) | 3 | 1000 | 10/06/2026, 14:17 | 1 | 252 | 251 | 252 | 439 | 436 | 437 | 185 mm² |  | 45 | 56 | 29 | 18 | 185 mm² |  | 21 | 18 | 37 | 19 | 185 mm² |  | 0 | 46 | 0 | 44 | 185 mm² |  | 59 | 54 | 61 | 19 | 185 mm² |  | 27 | 47 | 40 | 26 | [62 empty] | Total Load R: 152; Total Load Y: 221; Total Load B: 167; Total Load N: 126 | 221 | 152 | 16.8042 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.410714, 56.740274 | 1085 | Pole (PMT) | 3 | 100 | 06/06/2026, 16:20 | 1 | 240 | 240 | 239 | 416 | 418 | 419 | 120 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN03 | 23.417353, 56.748635 | 1084 | Pole (PMT) | 3 | 315 | 06/06/2026, 16:16 | 1 | 239 | 240 | 238 | 416 | 412 | 414 | 185 mm² |  | 18 | 18 | 18 | 0 | 120 mm² |  | 180 | 130 | 130 | 48 | [80 empty] | Total Load R: 198; Total Load Y: 148; Total Load B: 148; Total Load N: 48 | 198 | 148 | 45.2907 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.42429, 56.755063 | 1080 | Pole (PMT) | 3 | 315 | 06/06/2026, 16:11 | 1 | 240 | 240 | 239 | 419 | 416 | 415 | 185 mm² |  | 43 | 37 | 52 | 14 | 120 mm² |  | 37 | 36 | 24 | 16 | [80 empty] | Total Load R: 80; Total Load Y: 73; Total Load B: 76; Total Load N: 30 | 80 | 73 | 18.4312 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN03 | 23.423919, 56.757073 | 1079 | Pole (PMT) | 3 | 100 | 06/06/2026, 16:06 | 1 | 234 | 235 | 234 | 412 | 407 | 405 | 120 mm² |  | 0 | 12 | 0 | 11 | 120 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 0; Total Load Y: 12; Total Load B: 0; Total Load N: 11 | 12 | 0 | 8.5633 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.427688, 56.7604 | 2278 | Pole (PMT) | 3 | 100 | 06/06/2026, 16:02 | 1 | 241 | 240 | 239 | 419 | 416 | 413 | 185 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 0 | 13 | 28 | 18 | [80 empty] | Total Load R: 0; Total Load Y: 13; Total Load B: 28; Total Load N: 18 | 28 | 0 | 20.3204 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.43239, 56.770355 | 1069 | Pole (PMT) | 3 | 200 | 06/06/2026, 15:56 | 1 | 238 | 239 | 237 | 413 | 411 | 414 | 120 mm² |  | 20 | 11 | 40 | 37 | 120 mm² |  | 32 | 60 | 19 | 37 | 185 mm² |  | 59 | 52 | 117 | 53 | [74 empty] | Total Load R: 111; Total Load Y: 123; Total Load B: 176; Total Load N: 127 | 176 | 111 | 62.9497 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.425409, 56.774155 | 4388 | Pole (PMT) | 3 | 100 | 06/06/2026, 15:47 | 1 | 240 | 241 | 242 | 420 | 419 | 418 | 185 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN03 | 23.426031, 56.771192 | 1385 | Pole (PMT) | 3 | 100 | 06/06/2026, 15:44 | 1 | 235 | 234 | 231 | 409 | 399 | 403 | 120 mm² |  | 69 | 89 | 115 | 38 | [86 empty] | Total Load R: 69; Total Load Y: 89; Total Load B: 115; Total Load N: 38 | 115 | 69 | 81.467 | Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.403031, 56.78022 | 1675 | Ground (GMT) | 3 | 500 | 06/06/2026, 15:22 | 1 | 236 | 235 | 236 | 412 | 408 | 409 | [12 empty] | 240 mm² |  | 29 | 32 | 20 | 18 | 240 mm² |  | 39 | 33 | 22 | 19 | 240 mm² |  | 42 | 44 | 14 | 20 | 185 mm² |  | 10 | 14 | 11 | 12 | [56 empty] | Total Load R: 120; Total Load Y: 123; Total Load B: 67; Total Load N: 69 | 123 | 67 | 17.5547 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.404978, 56.778611 | 1593 | Pole (PMT) | 3 | 100 | 06/06/2026, 15:16 | 1 | 234 | 234 | 233 | 407 | 403 | 404 | 185 mm² |  | 11 | 24 | 39 | 17 | 240 mm² |  | 51 | 42 | 13 | 27 | [80 empty] | Total Load R: 62; Total Load Y: 66; Total Load B: 52; Total Load N: 44 | 66 | 52 | 46.5263 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN03 | 23.408875, 56.779751 | 4628 | Pole (PMT) | 3 | 100 | 06/06/2026, 15:11 | 1 | 237 | 237 | 235 | 412 | 408 | 410 | 185 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN03 | 23.410059, 56.775618 | 1075 | Ground (GMT) | 3 | 1000 | 06/06/2026, 15:07 | 1 | 234 | 237 | 234 | 407 | 405 | 409 | [12 empty] | 240 mm² |  | 26 | 29 | 32 | 0 | 185 mm² |  | 51 | 0 | 26 | 37 | 185 mm² |  | 48 | 46 | 0 | 44 | 185 mm² |  | 140 | 80 | 131 | 53 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 62 | 33 | 61 | 34 | [44 empty] | Total Load R: 327; Total Load Y: 188; Total Load B: 250; Total Load N: 168 | 327 | 188 | 23.0517 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.415399, 56.776525 | 416 | Pole (PMT) | 3 | 100 | 06/06/2026, 14:53 | 1 | 246 | 248 | 246 | 430 | 425 | 431 | 120 mm² |  | 39 | 23 | 45 | 19 | [86 empty] | Total Load R: 39; Total Load Y: 23; Total Load B: 45; Total Load N: 19 | 45 | 23 | 33.5152 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.417051, 56.770212 | 4373 | Pole (PMT) | 3 | 100 | 06/06/2026, 14:48 | 1 | 240 | 241 | 239 | 417 | 419 | 415 | 120 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN03 | 23.416404, 56.767033 | 1074 | Pole (PMT) | 3 | 100 | 06/06/2026, 14:39 | 1 | 237 | 239 | 237 | 414 | 410 | 412 | 120 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN03 | 23.423824, 56.766228 | 1073 | Pole (PMT) | 3 | 315 | 06/06/2026, 14:34 | 1 | 236 | 238 | 235 | 407 | 410 | 407 | 120 mm² |  | 36 | 37 | 48 | 16 | 120 mm² |  | 135 | 126 | 119 | 19 | 185 mm² |  | 94 | 35 | 109 | 66 | [74 empty] | Total Load R: 265; Total Load Y: 198; Total Load B: 276; Total Load N: 101 | 276 | 198 | 61.7666 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.430125, 56.764272 | 1072 | Pole (PMT) | 3 | 100 | 06/06/2026, 14:28 | 1 | 242 | 239 | 240 | 415 | 418 | 414 | 120 mm² |  | 0 | 12 | 10 | 13 | [86 empty] | Total Load R: 0; Total Load Y: 12; Total Load B: 10; Total Load N: 13 | 12 | 0 | 8.6256 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.430792, 56.767596 | 1071 | Ground (GMT) | 3 | 1000 | 06/06/2026, 14:22 | 1 | 236 | 236 | 237 | 408 | 411 | 410 | 120 mm² |  | 62 | 46 | 11 | 33 | [24 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 158 | 158 | 137 | 22 | 120 mm² |  | 33 | 43 | 48 | 17 | [44 empty] | Total Load R: 253; Total Load Y: 247; Total Load B: 196; Total Load N: 72 | 253 | 196 | 17.8789 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN03 | 23.433961, 56.766329 | 1742 | Pole (PMT) | 3 | 315 | 06/06/2026, 17:38 | 1 | 242 | 242 | 243 | 421 | 419 | 418 | 120 mm² |  | 31 | 0 | 7 | 25 | 120 mm² |  | 20 | 22 | 19 | 15 | [80 empty] | Total Load R: 51; Total Load Y: 22; Total Load B: 26; Total Load N: 40 | 51 | 22 | 11.806 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.431412, 56.763782 | 1390 | Pole (PMT) | 3 | 315 | 06/06/2026, 14:07 | 1 | 243 | 242 | 242 | 422 | 419 | 419 | 185 mm² |  | 83 | 49 | 69 | 26 | [86 empty] | Total Load R: 83; Total Load Y: 49; Total Load B: 69; Total Load N: 26 | 83 | 49 | 19.2593 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.433591, 56.761174 | 1076 | Pole (PMT) | 3 | 315 | 06/06/2026, 13:59 | 1 | 243 | 242 | 243 | 422 | 419 | 420 | 120 mm² |  | 190 | 165 | 33 | 39 | 120 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 190; Total Load Y: 165; Total Load B: 33; Total Load N: 39 | 190 | 33 | 44.0876 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.430164, 56.762053 | 2225 | Pole (PMT) | 3 | 315 | 06/06/2026, 13:55 | 1 | 246 | 245 | 245 | 426 | 425 | 425 | 185 mm² |  | 64 | 29 | 48 | 31 | 185 mm² |  | 60 | 32 | 75 | 32 | [80 empty] | Total Load R: 124; Total Load Y: 61; Total Load B: 123; Total Load N: 63 | 124 | 61 | 29.0457 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.431398, 56.758111 | 1078 | Ground (GMT) | 5 | 500 | 06/06/2026, 13:50 | 1 | 255 | 258 | 258 | 447 | 447 | 447 | 120 mm² |  | 198 | 240 | 138 | 73 | 120 mm² |  | 94 | 107 | 78 | 29 | 120 mm² |  | 93 | 34 | 30 | 55 | [74 empty] | Total Load R: 385; Total Load Y: 381; Total Load B: 246; Total Load N: 157 | 385 | 246 | 59.6155 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.427068, 56.750827 | 4143 | Pole (PMT) | 3 | 315 | 06/06/2026, 13:40 | 1 | 259 | 260 | 260 | 452 | 449 | 452 | 185 mm² |  | 81 | 87 | 80 | 10 | [86 empty] | Total Load R: 81; Total Load Y: 87; Total Load B: 80; Total Load N: 10 | 87 | 80 | 21.6226 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN03 | 23.430697, 56.751855 | 1081 | Pole (PMT) | 3 | 315 | 06/06/2026, 13:34 | 1 | 247 | 248 | 248 | 430 | 429 | 430 | 185 mm² |  | 2 | 26 | 31 | 28 | 185 mm² |  | 52 | 55 | 11 | 11 | [80 empty] | Total Load R: 54; Total Load Y: 81; Total Load B: 42; Total Load N: 39 | 81 | 42 | 19.1515 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.438472, 56.757619 | 1077 | Pole (PMT) | 3 | 100 | 06/06/2026, 13:27 | 1 | 250 | 250 | 250 | 435 | 434 | 435 | 120 mm² |  | 30 | 29 | 30 | 0 | 120 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 30; Total Load Y: 29; Total Load B: 30; Total Load N: 0 | 30 | 29 | 22.6033 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN03 | 23.439429, 56.749283 | 4201 | Pole (PMT) | 3 | 100 | 06/06/2026, 13:22 | 1 | 253 | 254 | 254 | 441 | 441 | 442 | 185 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN02 | 23.425442, 56.734912 | 983 | Pole (PMT) | 3 | 100 | 06/06/2026, 17:48 | 1 | 230 | 229 | 228 | 408 | 407 | 406 | 120 mm² |  | 55 | 36 | 26 | 35 | 185 mm² |  | 20 | 3 | 4 | 19 | [80 empty] | Total Load R: 75; Total Load Y: 39; Total Load B: 30; Total Load N: 54 | 75 | 30 | 53.0008 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN02 | 23.423389, 56.733645 | 308 | Pole (PMT) | 3 | 100 | 04/06/2026, 15:41 | 1 | 241 | 244 | 243 | 420 | 422 | 424 | [6 empty] | 120 mm² |  | 58 | 35 | 36 | 20 | [80 empty] | Total Load R: 58; Total Load Y: 35; Total Load B: 36; Total Load N: 20 | 58 | 35 | 42.1928 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN02 | 23.426723, 56.73619 | 984 | Pole (PMT) | 3 | 315 | 04/06/2026, 15:36 | 1 | 242 | 240 | 241 | 424 | 423 | 420 | 120 mm² |  | 22 | 18 | 15 | 17 | [86 empty] | Total Load R: 22; Total Load Y: 18; Total Load B: 15; Total Load N: 17 | 22 | 15 | 5.1291 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN02 | 23.432859, 56.742076 | 985 | Ground (GMT) | 3 | 1000 | 04/06/2026, 15:30 | 1 | 243 | 243 | 244 | 423 | 426 | 424 | 185 mm² |  | 13 | 9 | 9 | 4 | 185 mm² |  | 133 | 125 | 134 | 22 | 185 mm² |  | 40 | 10 | 22 | 32 | 185 mm² |  | 50 | 35 | 25 | 16 | 185 mm² |  | 38 | 15 | 15 | 27 | 185 mm² |  | 42 | 25 | 25 | 37 | [56 empty] | Total Load R: 316; Total Load Y: 219; Total Load B: 230; Total Load N: 138 | 316 | 219 | 23.152 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN02 | 23.432211, 56.742815 | 986 | Pole (PMT) | 3 | 100 | 04/06/2026, 15:26 | 1 | 232 | 233 | 233 | 405 | 402 | 405 | 120 mm² |  | 14 | 2 | 2 | 0 | 120 mm² |  | 8 | 8 | 0 | 0 | [80 empty] | Total Load R: 22; Total Load Y: 10; Total Load B: 2; Total Load N: 0 | 22 | 2 | 15.4326 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN02 | 23.434923, 56.744698 | 987 | Pole (PMT) | 3 | 315 | 04/06/2026, 15:22 | 1 | 240 | 241 | 242 | 421 | 418 | 418 | 120 mm² |  | 129 | 110 | 80 | 44 | 120 mm² |  | 101 | 85 | 116 | 32 | [80 empty] | Total Load R: 230; Total Load Y: 195; Total Load B: 196; Total Load N: 76 | 230 | 195 | 53.2427 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN02 | 23.436532, 56.745618 | 989 | Pole (PMT) | 3 | 200 | 04/06/2026, 15:17 | 1 | 243 | 243 | 222 | 424 | 422 | 424 | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 22 | 42 | 40 | 13 | [80 empty] | Total Load R: 22; Total Load Y: 42; Total Load B: 40; Total Load N: 13 | 42 | 22 | 15.4222 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN03 | 23.437968, 56.743489 | 990 | Pole (PMT) | 3 | 100 | 04/06/2026, 15:11 | 1 | 230 | 232 | 228 | 400 | 398 | 408 | 120 mm² |  | 24 | 10 | 36 | 31 | [86 empty] | Total Load R: 24; Total Load Y: 10; Total Load B: 36; Total Load N: 31 | 36 | 10 | 24.9415 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN02 | 23.437968, 56.743489 | 991 | Ground (GMT) | 3 | 1000 | 04/06/2026, 15:06 | 1 | 243 | 244 | 243 | 422 | 424 | 425 | [18 empty] | 185 mm² |  | 21 | 18 | 28 | 11 | 185 mm² |  | 135 | 127 | 137 | 19 | 185 mm² |  | 66 | 63 | 62 | 14 | [56 empty] | Total Load R: 222; Total Load Y: 208; Total Load B: 227; Total Load N: 44 | 227 | 208 | 16.592 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN02 | 23.428849, 56.733967 | 2140 | Pole (PMT) | 3 | 315 | 04/06/2026, 14:59 | 1 | 244 | 245 | 246 | 426 | 424 | 425 | 185 mm² |  | 99 | 125 | 81 | 34 | [86 empty] | Total Load R: 99; Total Load Y: 125; Total Load B: 81; Total Load N: 34 | 125 | 81 | 29.2799 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN02 | 23.43087, 56.726834 | 1488 | Pole (PMT) | 3 | 315 | 04/06/2026, 14:54 | 1 | 246 | 246 | 245 | 428 | 425 | 429 | 120 mm² |  | 68 | 135 | 137 | 25 | 185 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 68; Total Load Y: 135; Total Load B: 137; Total Load N: 25 | 137 | 68 | 32.2414 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN01 | 23.440034, 56.704097 | 1785 | Ground (GMT) | 3 | 1000 | 04/06/2026, 14:43 | 1 | 245 | 245 | 246 | 426 | 428 | 428 | [18 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | [18 empty] | 185 mm² |  | 13 | 9 | 4 | 11 | [44 empty] | Total Load R: 13; Total Load Y: 9; Total Load B: 4; Total Load N: 11 | 13 | 4 | 0.95921 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN01 | 23.443035, 56.702619 | 1493 | Pole (PMT) | 3 | 100 | 04/06/2026, 14:37 | 1 | 244 | 240 | 242 | 418 | 421 | 420 | 185 mm² |  | 18 | 48 | 65 | 35 | 120 mm² |  | 11 | 54 | 28 | 50 | [80 empty] | Total Load R: 29; Total Load Y: 102; Total Load B: 93; Total Load N: 85 | 102 | 29 | 73.8477 | Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN01 | 23.438893, 56.7051 | 959 | Pole (PMT) | 3 | 315 | 04/06/2026, 14:33 | 1 | 245 | 245 | 246 | 425 | 426 | 425 | 120 mm² |  | 95 | 85 | 40 | 35 | [86 empty] | Total Load R: 95; Total Load Y: 85; Total Load B: 40; Total Load N: 35 | 95 | 40 | 22.2005 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN01 | 23.437675, 56.711781 | 1372 | Pole (PMT) | 3 | 100 | 04/06/2026, 14:29 | 1 | 244 | 243 | 245 | 421 | 426 | 425 | 185 mm² |  | 53 | 60 | 15 | 35 | [86 empty] | Total Load R: 53; Total Load Y: 60; Total Load B: 15; Total Load N: 35 | 60 | 15 | 43.7516 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN01 | 23.440138, 56.713496 | 1754 | Ground (GMT) | 3 | 1000 | 04/06/2026, 14:23 | 1 | 253 | 253 | 254 | 440 | 441 | 442 | [12 empty] | 185 mm² |  | 17 | 35 | 23 | 13 | 185 mm² |  | 109 | 40 | 95 | 49 | 185 mm² |  | 15 | 18 | 13 | 3 | 185 mm² |  | 12 | 8 | 12 | 9 | [56 empty] | Total Load R: 153; Total Load Y: 101; Total Load B: 143; Total Load N: 74 | 153 | 101 | 11.6602 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN01 | 23.444518, 56.717975 | 4363 | Pole (PMT) | 3 | 100 | 04/06/2026, 14:17 | 1 | 248 | 249 | 249 | 433 | 434 | 434 | 185 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN01 | 23.444145, 56.717296 | 2070 | Pole (PMT) | 3 | 315 | 04/06/2026, 14:15 | 1 | 247 | 248 | 247 | 432 | 432 | 431 | 185 mm² |  | 23 | 10 | 28 | 16 | 185 mm² |  | 0 | 0 | 0 | 0 | [80 empty] | Total Load R: 23; Total Load Y: 10; Total Load B: 28; Total Load N: 16 | 28 | 10 | 6.6511 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN01 | 23.441236, 56.709882 | 958 | Pole (PMT) | 3 | 100 | 04/06/2026, 14:08 | 1 | 248 | 249 | 248 | 433 | 434 | 432 | 120 mm² |  | 0 | 0 | 0 | 0 | [86 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN01 | 23.440825, 56.709762 | 4336 | Pole (PMT) | 3 | 100 | 04/06/2026, 14:06 | 1 | 249 | 249 | 248 | 433 | 432 | 433 | 185 mm² |  | 5 | 9 | 11 | 15 | [86 empty] | Total Load R: 5; Total Load Y: 9; Total Load B: 11; Total Load N: 15 | 11 | 5 | 8.2498 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN01 | 23.437959, 56.708933 | 0858 | Ground (GMT) | 3 | 1000 | 04/06/2026, 14:03 | 1 | 249 | 249 | 250 | 433 | 433 | 434 | 185 mm² |  | 91 | 103 | 71 | 19 | 185 mm² |  | 26 | 48 | 19 | 23 | 185 mm² |  | 85 | 60 | 67 | 22 | [74 empty] | Total Load R: 202; Total Load Y: 211; Total Load B: 157; Total Load N: 64 | 211 | 157 | 15.8245 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN01 | 23.431697, 56.710769 | 2251 | Pole (PMT) | 3 | 315 | 04/06/2026, 13:57 | 1 | 242 | 241 | 243 | 424 | 425 | 423 | 185 mm² |  | 0 |  |  |  | 185 mm² |  | 155 | 61 | 96 | 77 | [80 empty] | Total Load R: 155; Total Load Y: 61; Total Load B: 96; Total Load N: 77 | 155 | 61 | 36.1366 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN01 | 23.435082, 56.706817 | 956 | Pole (PMT) | 3 | 200 | 04/06/2026, 13:52 | 1 | 250 | 248 | 249 | 431 | 434 | 433 | 120 mm² |  | 32 | 64 | 33 | 28 | 120 mm² |  | 77 | 121 | 97 | 24 | [80 empty] | Total Load R: 109; Total Load Y: 185; Total Load B: 130; Total Load N: 52 | 185 | 109 | 69.0525 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN01 | 23.434233, 56.710408 | 1734 | Pole (PMT) | 3 | 100 | 04/06/2026, 13:49 | 1 | 247 | 248 | 247 | 432 | 435 | 431 | 185 mm² |  | 36 | 46 | 45 | 11 | 185 mm² |  | 40 | 18 | 26 | 17 | [80 empty] | Total Load R: 76; Total Load Y: 64; Total Load B: 71; Total Load N: 28 | 76 | 64 | 56.8667 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN01 | 23.429686, 56.711633 | 954 | Pole (PMT) | 3 | 315 | 04/06/2026, 13:45 | 1 | 252 | 252 | 253 | 440 | 441 | 442 | 120 mm² |  | 18 | 15 | 22 | 12 | 120 mm² |  | 30 | 39 | 39 | 11 | [80 empty] | Total Load R: 48; Total Load Y: 54; Total Load B: 61; Total Load N: 23 | 61 | 48 | 14.7582 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN01 | 23.433834, 56.712691 | 955 | Pole (PMT) | 3 | 315 | 04/06/2026, 13:40 | 1 | 251 | 252 | 251 | 437 | 439 | 438 | 120 mm² |  | 50 | 65 | 52 | 13 | 120 mm² |  | 84 | 55 | 111 | 65 | 185 mm² |  | 42 | 51 | 35 | 23 | [74 empty] | Total Load R: 176; Total Load Y: 171; Total Load B: 198; Total Load N: 101 | 198 | 171 | 47.577 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN01 | 23.430754, 56.715042 | 2296 | Ground (GMT) | 3 | 1000 | 04/06/2026, 13:34 | 1 | 254 | 254 | 255 | 442 | 441 | 443 | [30 empty] | 185 mm² |  | 61 | 83 | 93 | 29 | 185 mm² |  | 122 | 90 | 93 | 31 | 185 mm² |  | 60 | 20 | 97 | 57 | [44 empty] | Total Load R: 243; Total Load Y: 193; Total Load B: 283; Total Load N: 117 | 283 | 193 | 21.6655 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN01 | 23.434275, 56.718539 | 952 | Pole (PMT) | 3 | 100 | 04/06/2026, 13:26 | 1 | 240 | 242 | 243 | 440 | 442 | 441 | 120 mm² |  | 8 | 9 | 5 | 3 | [86 empty] | Total Load R: 8; Total Load Y: 9; Total Load B: 5; Total Load N: 3 | 9 | 5 | 6.8589 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN01 | 23.430747, 56.718345 | 951 | Pole (PMT) | 3 | 315 | 04/06/2026, 13:19 | 1 | 253 | 254 | 253 | 440 | 441 | 440 | 120 mm² |  | 84 | 96 | 61 | 23 | 120 mm² |  | 109 | 124 | 112 | 24 | [80 empty] | Total Load R: 193; Total Load Y: 220; Total Load B: 173; Total Load N: 47 | 220 | 173 | 53.2262 | OK - No Upgrade | Need to Balance
Hijermat | HUGERMAT | K_LN01 | 23.430676, 56.718361 | 953 | Pole (PMT) | 3 | 315 | 04/06/2026, 13:15 | 1 | 254 | 254 | 255 | 443 | 444 | 442 | 120 mm² | [5 empty] | 120 mm² |  | 154 | 157 | 150 | 13 | [80 empty] | Total Load R: 154; Total Load Y: 157; Total Load B: 150; Total Load N: 13 | 157 | 150 | 38.2431 | OK - No Upgrade | OK - Balanced
Hijermat | HUGERMAT | K_LN2 | 23.519703, 56.750827 | 1177 | Pole (PMT) |  | 315 | 23/05/2026, 15:19 | 1 | 238 | 237 | 236 | 410 | 412 | 410 | 120 mm² |  | 38 | 48 | 57 | 15 | [86 empty] | Total Load R: 38; Total Load Y: 48; Total Load B: 57; Total Load N: 15 | 57 | 38 | 12.8502 | OK - No Upgrade | Need to Balance

## AMLAH
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Wadi Alain | AMLAH | K_LN2 | 23.222521, 56.990387 | 2121 | Pole (PMT) | 3 | 315 | 12/06/2026, 15:54 | 1 | 229 | 232 | 230 | 401 | 397 | 402 | 185 mm² |  | 20 | 15 | 21 | 11 | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 20; Total Load Y: 15; Total Load B: 21; Total Load N: 11 | 21 | 15 | 4.6303 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN2 | 23.222562, 56.987955 | 2095 | Ground (GMT) | 3 | 1000 | 12/06/2026, 15:49 | 1 | 229 | 230 | 228 | 400 | 396 | 402 | [36 empty] | 185 mm² |  | 40 | 80 | 67 | 33 | 185 mm² |  | 67 | 62 | 53 | 11 | 107 | 142 | 120 | 44 | 142 | 107 | 9.838 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN2 | 23.21762, 56.990657 | 1334 | Ground (GMT) | 3 | 500 | 12/06/2026, 15:42 | 1 | 232 | 228 | 229 | 399 | 401 | 395 | [12 empty] | 185 mm² |  | 0 | 18 | 0 | 14 | 185 mm² |  | 26 | 22 | 28 | 20 | 185 mm² |  | 69 | 80 | 126 | 37 | 185 mm² |  | 27 | 22 | 20 | 24 | [8 empty] | Total Load R: 122; Total Load Y: 142; Total Load B: 174; Total Load N: 95 | 174 | 122 | 24.0499 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN2 | 23.215544, 56.989445 | 2065 | Pole (PMT) | 3 | 315 | 12/06/2026, 15:33 | 1 | 229 | 232 | 230 | 401 | 395 | 401 | 185 mm² |  | 36 | 12 | 18 | 22 | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 36; Total Load Y: 12; Total Load B: 18; Total Load N: 22 | 36 | 12 | 7.9377 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN2 | 23.219488, 56.987038 | 2183 | Ground (GMT) | 3 | 500 | 12/06/2026, 15:26 | 1 | 230 | 232 | 230 | 402 | 396 | 401 | [12 empty] | 185 mm² |  | 9 | 8 | 23 | 9 | 185 mm² |  | 35 | 37 | 42 | 11 | 185 mm² |  | 15 | 70 | 35 | 18 | 185 mm² |  | 19 | 23 | 21 | 10 | [8 empty] | Total Load R: 78; Total Load Y: 138; Total Load B: 121; Total Load N: 48 | 138 | 78 | 19.2175 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN2 | 23.216748, 56.984575 | 1570 | Pole (PMT) | 3 | 100 | 12/06/2026, 15:20 | 1 | 230 | 233 | 230 | 402 | 397 | 404 | 185 mm² |  | 15 | 0 | 9 | 8 | [38 empty] | Total Load R: 15; Total Load Y: 0; Total Load B: 9; Total Load N: 8 | 15 | 0 | 10.4443 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN2 | 23.226447, 56.982546 | 719 | Pole (PMT) | 3 | 315 | 12/06/2026, 15:13 | 1 | 230 | 233 | 232 | 402 | 398 | 404 | 120 mm² |  | 82 | 66 | 57 | 19 | 185 mm² |  | 83 | 43 | 72 | 27 | [32 empty] | Total Load R: 165; Total Load Y: 109; Total Load B: 129; Total Load N: 46 | 165 | 109 | 36.472 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN2 | 23.223188, 56.981574 | 718 | Pole (PMT) | 3 | 50 | 12/06/2026, 15:09 | 1 | 230 | 233 | 228 | 401 | 394 | 403 | 120 mm² |  | 16 | 14 | 36 | 24 | [38 empty] | Total Load R: 16; Total Load Y: 14; Total Load B: 36; Total Load N: 24 | 36 | 14 | 50.0078 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN2 | 23.222308, 56.977228 | 04360 | Pole (PMT) | 3 | 50 | 12/06/2026, 15:06 | 1 | 233 | 236 | 235 | 408 | 406 | 410 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN2 | 23.220297, 56.972085 | 2154 | Pole (PMT) | 3 | 100 | 12/06/2026, 15:03 | 1 | 234 | 237 | 236 | 410 | 407 | 413 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN2 | 23.217651, 56.969428 | 717 | Pole (PMT) | 3 | 200 | 12/06/2026, 15:00 | 1 | 251 | 249 | 250 | 435 | 438 | 431 | 50 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN2 | 23.215317, 56.966462 | 2041 | Pole (PMT) | 3 | 315 | 12/06/2026, 14:54 | 1 | 237 | 240 | 238 | 416 | 412 | 416 | 185 mm² |  | 30 | 18 | 44 | 18 | [38 empty] | Total Load R: 30; Total Load Y: 18; Total Load B: 44; Total Load N: 18 | 44 | 18 | 10.0646 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN2 | 23.213219, 56.964461 | 716 | Ground (GMT) | 4 | 1000 | 12/06/2026, 14:50 | 1 | 238 | 240 | 239 | 416 | 412 | 417 | [6 empty] | 185 mm² |  | 84 | 101 | 139 | 41 | 185 mm² |  | 33 | 53 | 55 | 19 | 185 mm² |  | 20 | 33 | 22 | 29 | 185 mm² |  | 25 | 35 | 41 | 28 | [14 empty] | Total Load R: 162; Total Load Y: 222; Total Load B: 257; Total Load N: 117 | 257 | 162 | 18.5177 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN2 | 23.193503, 56.919765 | 704 | Pole (PMT) | 3 | 100 | 12/06/2026, 14:39 | 1 | 234 | 233 | 233 | 406 | 403 | 404 | 185 mm² |  | 48 | 71 | 96 | 57 | [38 empty] | Total Load R: 48; Total Load Y: 71; Total Load B: 96; Total Load N: 57 | 96 | 48 | 67.5084 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN2 | 23.183104, 56.920296 | 703 | Pole (PMT) | 3 | 315 | 12/06/2026, 14:34 | 1 | 250 | 249 | 250 | 434 | 435 | 433 | 120 mm² | [5 empty] | 120 mm² |  | 100 | 109 | 115 | 20 | [32 empty] | Total Load R: 100; Total Load Y: 109; Total Load B: 115; Total Load N: 20 | 115 | 100 | 27.4434 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN2 | 23.181422, 56.921566 | 2175 | Pole (PMT) | 3 | 315 | 12/06/2026, 14:30 | 1 | 252 | 252 | 253 | 437 | 440 | 438 | 185 mm² |  | 18 | 20 | 11 | 24 | [38 empty] | Total Load R: 18; Total Load Y: 20; Total Load B: 11; Total Load N: 24 | 20 | 11 | 4.8058 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN2 |  | 702 | Pole (PMT) | 3 | 315 | 12/06/2026, 14:25 | 1 | 250 | 251 | 252 | 436 | 437 | 438 | 120 mm² |  | 181 | 120 | 136 | 44 | [38 empty] | Total Load R: 181; Total Load Y: 120; Total Load B: 136; Total Load N: 44 | 181 | 120 | 43.3925 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.208249, 56.947645 | 2042 | Pole (PMT) | 3 | 200 | 09/06/2026, 15:31 | 1 | 248 | 247 | 246 | 431 | 428 | 429 | 185 mm² |  | 102 | 116 | 130 | 21 | [38 empty] | Total Load R: 102; Total Load Y: 116; Total Load B: 130; Total Load N: 21 | 130 | 102 | 48.5234 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.210232, 56.950534 | 715 | Pole (PMT) | 3 | 100 | 09/06/2026, 15:27 | 1 | 242 | 243 | 243 | 422 | 420 | 422 | 120 mm² |  | 12 | 18 | 9 | 10 | 120 mm² |  | 160 | 155 | 194 | 32 | [32 empty] | Total Load R: 172; Total Load Y: 173; Total Load B: 203; Total Load N: 42 | 203 | 172 | 148.3779 | Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.212488, 56.947376 | 714 | Pole (PMT) | 3 | 315 | 09/06/2026, 15:24 | 1 | 243 | 243 | 244 | 423 | 424 | 421 | 240 mm² |  | 126 | 141 | 74 | 71 | [38 empty] | Total Load R: 126; Total Load Y: 141; Total Load B: 74; Total Load N: 71 | 141 | 74 | 32.7951 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.212057, 56.94642 | 1750 | Pole (PMT) | 3 | 315 | 09/06/2026, 15:21 | 1 | 250 | 252 | 251 | 436 | 437 | 437 | 185 mm² |  | 54 | 8 | 7 | 45 | [38 empty] | Total Load R: 54; Total Load Y: 8; Total Load B: 7; Total Load N: 45 | 54 | 7 | 12.9458 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.214423, 56.94636 | 4569 | Pole (PMT) | 3 | 100 | 09/06/2026, 15:13 | 1 | 252 | 253 | 251 | 440 | 437 | 437 | 120 mm² |  | 1 | 1 | 3 | 1 | 185 mm² |  | 1 | 1 | 3 | 1 | [32 empty] | Total Load R: 2; Total Load Y: 2; Total Load B: 6; Total Load N: 2 | 6 | 2 | 4.5726 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.20755, 56.955553 | 4744 | Pole (PMT) | 3 | 100 | 09/06/2026, 15:03 | 1 | 250 | 252 | 251 | 436 | 435 | 436 | 185 mm² |  | 26 | 9 | 22 | 13 | [38 empty] | Total Load R: 26; Total Load Y: 9; Total Load B: 22; Total Load N: 13 | 26 | 9 | 19.6345 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.20755, 56.955553 | 713 | Pole (PMT) | 3 | 100 | 09/06/2026, 14:59 | 1 | 250 | 254 | 253 | 440 | 437 | 439 | 120 mm² |  | 107 | 85 | 88 | 23 | 185 mm² |  | 2 | 19 | 17 | 13 | [32 empty] | Total Load R: 109; Total Load Y: 104; Total Load B: 105; Total Load N: 36 | 109 | 104 | 83.0692 | Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN3 | 23.210538, 56.96312 | 712 | Ground (GMT) | 3 | 1000 | 09/06/2026, 14:53 | 1 | 250 | 251 | 251 | 435 | 434 | 436 | [12 empty] | 185 mm² |  | 52 | 25 | 16 | 23 | 185 mm² |  | 202 | 134 | 192 | 52 | 185 mm² |  | 147 | 210 | 193 | 43 | [14 empty] | Total Load R: 401; Total Load Y: 369; Total Load B: 401; Total Load N: 118 | 401 | 369 | 30.213 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN3 | 23.207629, 56.959494 | 711 | Pole (PMT) | 3 | 200 | 09/06/2026, 14:47 | 1 | 249 | 249 | 250 | 434 | 435 | 432 | 120 mm² |  | 113 | 73 | 45 | 48 | 120 mm² |  | 12 | 47 | 24 | 21 | [32 empty] | Total Load R: 125; Total Load Y: 120; Total Load B: 69; Total Load N: 69 | 125 | 69 | 46.9819 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.207629, 56.959494 | 2350 | Pole (PMT) | 3 | 315 | 09/06/2026, 14:43 | 1 | 252 | 251 | 252 | 438 | 439 | 437 | 185 mm² |  | 77 | 85 | 71 | 18 | [38 empty] | Total Load R: 77; Total Load Y: 85; Total Load B: 71; Total Load N: 18 | 85 | 71 | 20.4712 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN3 | 23.202293, 56.943808 | 710 | Pole (PMT) | 3 | 100 | 09/06/2026, 14:41 | 1 | 246 | 246 | 247 | 428 | 430 | 429 | 120 mm² |  | 3 | 3 | 3 | 2 | 185 mm² |  | 11 | 9 | 8 | 4 | [32 empty] | Total Load R: 14; Total Load Y: 12; Total Load B: 11; Total Load N: 6 | 14 | 11 | 10.3784 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.202293, 56.943808 | 709 | Pole (PMT) | 3 | 100 | 09/06/2026, 14:37 | 1 | 242 | 241 | 242 | 420 | 420 | 419 | 50 mm² |  | 10 | 9 | 11 | 5 | [38 empty] | Total Load R: 10; Total Load Y: 9; Total Load B: 11; Total Load N: 5 | 11 | 9 | 8.0021 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN3 | 23.202293, 56.943808 | 2320 | Pole (PMT) | 3 | 315 | 09/06/2026, 14:34 | 1 | 253 | 253 | 254 | 441 | 442 | 441 | 185 mm² |  | 18 | 30 | 9 | 22 | [38 empty] | Total Load R: 18; Total Load Y: 30; Total Load B: 9; Total Load N: 22 | 30 | 9 | 7.2746 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.202293, 56.943808 | 708 | Ground (GMT) | 3 | 1000 | 09/06/2026, 14:30 | 1 | 251 | 251 | 252 | 437 | 436 | 436 | [30 empty] | 185 mm² |  | 20 | 38 | 80 | 58 | 185 mm² |  | 41 | 36 | 33 | 11 | 185 mm² |  | 75 | 88 | 63 | 36 | 136 | 162 | 176 | 105 | 176 | 136 | 13.3215 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.185382, 56.930585 | 04314 | Pole (PMT) | 3 | 100 | 09/06/2026, 14:26 | 1 | 248 | 248 | 251 | 431 | 435 | 432 | 185 mm² |  | 73 | 72 | 28 | 53 | [38 empty] | Total Load R: 73; Total Load Y: 72; Total Load B: 28; Total Load N: 53 | 73 | 28 | 54.4955 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.185382, 56.930585 | 707 | Pole (PMT) | 3 | 315 | 09/06/2026, 14:22 | 1 | 251 | 252 | 252 | 434 | 436 | 437 | 120 mm² |  | 94 | 76 | 62 | 31 | 120 mm² |  | 47 | 38 | 55 | 18 | [32 empty] | Total Load R: 141; Total Load Y: 114; Total Load B: 117; Total Load N: 49 | 141 | 114 | 33.648 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.180326, 56.94426 | 705 | Pole (PMT) | 3 | 100 | 09/06/2026, 14:19 | 1 | 252 | 251 | 252 | 444 | 445 | 445 | 120 mm² |  | 1 | 1 | 3 | 1 | [38 empty] | Total Load R: 1; Total Load Y: 1; Total Load B: 3; Total Load N: 1 | 3 | 1 | 2.3071 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.18532, 56.930545 | 1383 | Pole (PMT) | 3 | 100 | 09/06/2026, 14:04 | 1 | 252 | 253 | 252 | 439 | 438 | 440 | 120 mm² |  | 1 | 2 | 9 | 9 | [38 empty] | Total Load R: 1; Total Load Y: 2; Total Load B: 9; Total Load N: 9 | 9 | 1 | 6.8433 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.191221, 56.927685 | 4774 | Pole (PMT) | 3 | 100 | 09/06/2026, 13:58 | 1 | 253 | 254 | 254 | 440 | 441 | 441 | 185 mm² |  | 3 | 5 | 5 | 1 | [38 empty] | Total Load R: 3; Total Load Y: 5; Total Load B: 5; Total Load N: 1 | 5 | 3 | 3.8105 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.17562, 56.918555 | 706 | Pole (PMT) | 3 | 100 | 09/06/2026, 13:54 | 1 | 253 | 254 | 254 | 440 | 441 | 443 | 120 mm² |  | 6 | 10 | 9 | 6 | [38 empty] | Total Load R: 6; Total Load Y: 10; Total Load B: 9; Total Load N: 6 | 10 | 6 | 7.621 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.17562, 56.918555 | 04801 | Ground (GMT) | 3 | 500 | 09/06/2026, 13:49 | 1 | 253 | 254 | 254 | 441 | 442 | 442 | 185 mm² |  | 46 | 59 | 37 | 25 | 185 mm² |  | 25 | 27 | 68 | 33 | [32 empty] | Total Load R: 71; Total Load Y: 86; Total Load B: 105; Total Load N: 58 | 105 | 71 | 16.0405 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN3 | 23.179355, 56.914401 | 701 | Pole (PMT) | 4 | 100 | 09/06/2026, 13:42 | 1 | 242 | 256 | 257 | 443 | 444 | 446 | 120 mm² |  | 9 | 12 | 9 | 13 | 120 mm² |  | 22 | 7 | 18 | 8 | [32 empty] | Total Load R: 31; Total Load Y: 19; Total Load B: 27; Total Load N: 21 | 31 | 19 | 23.7863 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.140594, 56.878859 | 821 | Pole (PMT) | 2 | 100 | 04/06/2026, 15:39 | 1 | 236 | 238 | 238 | 412 | 411 | 410 | 120 mm² |  | 145 | 120 | 112 | 29 | [38 empty] | Total Load R: 145; Total Load Y: 120; Total Load B: 112; Total Load N: 29 | 145 | 112 | 103.4727 | Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.132371, 56.881862 | 820 | Pole (PMT) | 3 | 315 | 04/06/2026, 15:34 | 1 | 240 | 243 | 242 | 420 | 421 | 419 | 120 mm² |  | 153 | 74 | 43 | 112 | 120 mm² |  | 73 | 30 | 70 | 36 | [32 empty] | Total Load R: 226; Total Load Y: 104; Total Load B: 113; Total Load N: 148 | 226 | 104 | 52.1925 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.131071, 56.88013 | 1845 | Pole (PMT) | 3 | 315 | 04/06/2026, 15:30 | 1 | 244 | 246 | 244 | 426 | 424 | 423 | 185 mm² |  | 14 | 13 | 14 | 8 | 185 mm² |  | 9 | 7 | 9 | 9 | [32 empty] | Total Load R: 23; Total Load Y: 20; Total Load B: 23; Total Load N: 17 | 23 | 20 | 5.3875 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN4 | 23.129754, 56.875266 | 819 | Ground (GMT) | 3 | 1000 | 04/06/2026, 15:26 | 1 | 243 | 244 | 243 | 423 | 420 | 421 | [30 empty] | 185 mm² |  | 106 | 105 | 84 | 29 | 185 mm² |  | 49 | 30 | 60 | 28 | 185 mm² |  | 58 | 66 | 93 | 28 | 213 | 201 | 237 | 85 | 237 | 201 | 17.364 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN4 | 23.132643, 56.890684 | 2187 | Pole (PMT) | 2 | 100 | 04/06/2026, 15:20 | 1 | 232 | 233 | 232 | 406 | 404 | 403 | 185 mm² |  | 5 | 2 | 4 | 4 | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 5; Total Load Y: 2; Total Load B: 4; Total Load N: 4 | 5 | 2 | 3.5161 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.121858, 56.914494 | 816 | Pole (PMT) | 3 | 315 | 04/06/2026, 15:13 | 1 | 242 | 244 | 241 | 422 | 421 | 417 | 120 mm² |  | 64 | 35 | 87 | 24 | [38 empty] | Total Load R: 64; Total Load Y: 35; Total Load B: 87; Total Load N: 24 | 87 | 35 | 20.1875 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.123088, 56.918728 | 815 | Pole (PMT) | 3 | 315 | 04/06/2026, 15:09 | 1 | 241 | 242 | 239 | 415 | 420 | 417 | 120 mm² |  | 92 | 118 | 150 | 33 | 120 mm² |  | 18 | 14 | 24 | 8 | [32 empty] | Total Load R: 110; Total Load Y: 132; Total Load B: 174; Total Load N: 41 | 174 | 110 | 39.7052 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.128975, 56.915604 | 1747 | Pole (PMT) | 5 | 200 | 04/06/2026, 15:00 | 1 | 249 | 251 | 250 | 434 | 432 | 434 | 185 mm² |  | 248 | 214 | 167 | 42 | [38 empty] | Total Load R: 248; Total Load Y: 214; Total Load B: 167; Total Load N: 42 | 248 | 167 | 93.212 | Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.134807, 56.917888 | 1438 | Pole (PMT) | 5 | 315 | 04/06/2026, 14:55 | 1 | 252 | 254 | 252 | 440 | 439 | 436 | 185 mm² |  | 66 | 62 | 68 | 12 | 185 mm² |  | 131 | 125 | 126 | 18 | [32 empty] | Total Load R: 197; Total Load Y: 187; Total Load B: 194; Total Load N: 30 | 197 | 187 | 47.6616 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN4 | 23.137999, 56.925044 | 814 | Pole (PMT) | 3 | 100 | 04/06/2026, 14:51 | 1 | 243 | 245 | 243 | 425 | 423 | 421 | 120 mm² |  | 10 | 17 | 5 | 16 | [38 empty] | Total Load R: 10; Total Load Y: 17; Total Load B: 5; Total Load N: 16 | 17 | 5 | 12.5141 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.137199, 56.920016 | 2102 | Pole (PMT) | 3 | 100 | 04/06/2026, 14:47 | 1 | 241 | 244 | 243 | 422 | 423 | 419 | 185 mm² |  | 36 | 8 | 5 | 28 | [38 empty] | Total Load R: 36; Total Load Y: 8; Total Load B: 5; Total Load N: 28 | 36 | 5 | 26.3133 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.138582, 56.917733 | 2040 | Pole (PMT) | 3 | 315 | 04/06/2026, 14:44 | 1 | 241 | 243 | 240 | 419 | 420 | 417 | 185 mm² |  | 160 | 82 | 143 | 96 | [38 empty] | Total Load R: 160; Total Load Y: 82; Total Load B: 143; Total Load N: 96 | 160 | 82 | 36.8624 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.135943, 56.915532 | 813 | Pole (PMT) | 3 | 200 | 04/06/2026, 14:40 | 1 | 240 | 240 | 239 | 416 | 414 | 414 | 120 mm² |  | 64 | 75 | 70 | 15 | 120 mm² |  | 73 | 109 | 77 | 29 | [32 empty] | Total Load R: 137; Total Load Y: 184; Total Load B: 147; Total Load N: 44 | 184 | 137 | 66.289 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.134189, 56.912685 | 4611 | Pole (PMT) | 3 | 100 | 04/06/2026, 14:37 | 1 | 239 | 241 | 238 | 418 | 417 | 411 | 185 mm² |  | 73 | 68 | 107 | 25 | [38 empty] | Total Load R: 73; Total Load Y: 68; Total Load B: 107; Total Load N: 25 | 107 | 68 | 77.4677 | Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.13353, 56.910042 | 1774 | Pole (PMT) | 3 | 315 | 04/06/2026, 14:33 | 1 | 243 | 245 | 244 | 425 | 424 | 422 | 185 mm² |  | 13 | 44 | 10 | 33 | [38 empty] | Total Load R: 13; Total Load Y: 44; Total Load B: 10; Total Load N: 33 | 44 | 10 | 10.2823 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.131846, 56.903807 | 812 | Pole (PMT) | 4 | 100 | 04/06/2026, 14:29 | 1 | 249 | 251 | 255 | 431 | 439 | 441 | 120 mm² |  | 51 | 24 | 10 | 33 | 185 mm² |  | 26 | 29 | 10 | 37 | [32 empty] | Total Load R: 77; Total Load Y: 53; Total Load B: 20; Total Load N: 70 | 77 | 20 | 57.4816 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.132593, 56.900242 | 1958 | Pole (PMT) | 3 | 100 | 04/06/2026, 14:26 | 1 | 242 | 242 | 242 | 419 | 421 | 421 | 120 mm² |  | 13 | 11 | 16 | 5 | [38 empty] | Total Load R: 13; Total Load Y: 11; Total Load B: 16; Total Load N: 5 | 16 | 11 | 11.6117 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.133856, 56.898407 | 811 | Pole (PMT) |  | 315 | 04/06/2026, 14:23 | 1 | 254 | 255 | 254 | 443 | 443 | 441 | 120 mm² |  | 54 | 105 | 113 | 44 | 120 mm² |  | 33 | 10 | 44 | 25 | [32 empty] | Total Load R: 87; Total Load Y: 115; Total Load B: 157; Total Load N: 69 | 157 | 87 | 38.2431 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.132037, 56.895632 | 4500 | Pole (PMT) | 3 | 100 | 04/06/2026, 14:19 | 1 | 244 | 244 | 241 | 423 | 423 | 421 | 120 mm² |  | 0 | 5 | 0 | 5 | [38 empty] | Total Load R: 0; Total Load Y: 5; Total Load B: 0; Total Load N: 5 | 5 | 0 | 3.6633 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.132265, 56.892597 | 810 | Pole (PMT) | 5 | 315 | 04/06/2026, 14:15 | 1 | 255 | 256 | 256 | 444 | 443 | 442 | 120 mm² |  | 110 | 140 | 113 | 35 | [38 empty] | Total Load R: 110; Total Load Y: 140; Total Load B: 113; Total Load N: 35 | 140 | 110 | 34.1791 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.121003, 56.888785 | 806 | Ground (GMT) | 3 | 1000 | 04/06/2026, 14:09 | 1 | 245 | 246 | 246 | 425 | 428 | 428 | [24 empty] | 185 mm² |  | 23 | 13 | 49 | 30 | 185 mm² |  | 69 | 52 | 69 | 13 | 185 mm² |  | 105 | 70 | 77 | 28 |  |  | Total Load R: 197; Total Load Y: 135; Total Load B: 195; Total Load N: 71 | 197 | 135 | 14.5016 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.117992, 56.894357 | 1804 | Ground (GMT) | 3 | 500 | 04/06/2026, 14:03 | 1 | 244 | 245 | 245 | 424 | 425 | 425 | [24 empty] | 185 mm² |  | 17 | 10 | 9 | 5 | 185 mm² |  | 4 | 25 | 38 | 24 | [8 empty] | Total Load R: 21; Total Load Y: 35; Total Load B: 47; Total Load N: 29 | 47 | 21 | 6.9033 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.117097, 56.889115 | 1482 | Pole (PMT) | 3 | 315 | 04/06/2026, 13:56 | 1 | 243 | 245 | 245 | 423 | 427 | 423 | 120 mm² |  | 119 | 110 | 89 | 32 | 120 mm² |  | 5 | 13 | 16 | 14 | [32 empty] | Total Load R: 124; Total Load Y: 123; Total Load B: 105; Total Load N: 46 | 124 | 105 | 28.8411 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN1 | 23.13794, 56.91178 | 4789 | Pole (PMT) |  | 100 | 30/05/2026, 15:55 | 1 | 246 | 245 | 245 | 426 | 428 | 423 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN1 | 23.167275, 56.916032 | 624 | Pole (PMT) |  | 315 | 30/05/2026, 15:50 | 1 | 244 | 243 | 244 | 422 | 423 | 420 | 120 mm² |  | 80 | 92 | 73 | 28 | 120 mm² |  | 47 | 36 | 41 | 14 | [32 empty] | Total Load R: 127; Total Load Y: 128; Total Load B: 114; Total Load N: 42 | 128 | 114 | 29.7011 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN1 | 23.176784, 56.916351 | 623 | Pole (PMT) |  | 315 | 30/05/2026, 15:46 | 1 | 247 | 245 | 246 | 426 | 427 | 424 | 185 mm² |  | 20 | 17 | 16 | 5 | 185 mm² |  | 4 | 5 | 6 | 5 | [32 empty] | Total Load R: 24; Total Load Y: 22; Total Load B: 22; Total Load N: 10 | 24 | 22 | 5.6217 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN1 | 23.186288, 56.894756 | 2311 | Pole (PMT) |  | 315 | 30/05/2026, 15:36 | 1 | 248 | 247 | 247 | 428 | 429 | 426 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN1 | 23.1723, 56.904623 | 620 | Pole (PMT) |  | 315 | 30/05/2026, 15:28 | 1 | 243 | 243 | 243 | 421 | 422 | 421 |  |  | 135 | 105 | 161 | 37 | 185 mm² |  | 129 | 79 | 78 | 48 | [32 empty] | Total Load R: 264; Total Load Y: 184; Total Load B: 239; Total Load N: 85 | 264 | 184 | 61.1134 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN1 | 23.17081, 56.90859 | 621 | Pole (PMT) |  | 315 | 30/05/2026, 15:23 | 1 | 245 | 245 | 243 | 425 | 423 | 423 | 120 mm² |  | 125 | 76 | 157 | 60 | 120 mm² |  | 38 | 25 | 76 | 50 | [32 empty] | Total Load R: 163; Total Load Y: 101; Total Load B: 233; Total Load N: 110 | 233 | 101 | 54.4496 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN1 | 23.174089, 56.907603 | 619 | Pole (PMT) |  | 315 | 30/05/2026, 15:17 | 1 | 243 | 240 | 242 | 420 | 420 | 419 | 120 mm² |  | 142 | 132 | 133 | 18 | 120 mm² |  | 76 | 109 | 85 | 29 | [32 empty] | Total Load R: 218; Total Load Y: 241; Total Load B: 218; Total Load N: 47 | 241 | 218 | 55.6566 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN1 | 23.164933, 56.905243 | 622 | Pole (PMT) |  | 315 | 24/05/2026, 15:23 | 1 | 247 | 248 | 245 | 429 | 429 | 428 | 120 mm² |  | 186 | 66 | 104 | 104 | 120 mm² |  | 15 | 8 | 22 | 11 | [32 empty] | Total Load R: 201; Total Load Y: 74; Total Load B: 126; Total Load N: 115 | 201 | 74 | 47.4137 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN1 | 23.161258, 56.912533 | 1641 | Pole (PMT) |  | 100 | 24/05/2026, 15:17 | 1 | 246 | 241 | 245 | 423 | 426 | 419 | 120 mm² |  | 18 | 47 | 26 | 28 | 185 mm² |  | 10 | 7 | 9 | 12 | [32 empty] | Total Load R: 28; Total Load Y: 54; Total Load B: 35; Total Load N: 40 | 54 | 28 | 39.5635 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN1 | 23.161258, 56.912533 | 625 | Pole (PMT) |  | 200 | 24/05/2026, 15:11 | 1 | 248 | 249 | 250 | 430 | 436 | 428 | 120 mm² |  | 182 | 144 | 134 | 46 |  |  | 190 | 172 | 145 | 27 | [32 empty] | Total Load R: 372; Total Load Y: 316; Total Load B: 279; Total Load N: 73 | 372 | 279 | 138.5294 | Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN1 | 23.157836, 56.911507 | 2078 | Pole (PMT) |  | 100 | 24/05/2026, 15:08 | 1 | 246 | 246 | 247 | 426 | 427 | 426 | 70 mm² |  | 14 | 5 | 5 | 12 | [38 empty] | Total Load R: 14; Total Load Y: 5; Total Load B: 5; Total Load N: 12 | 14 | 5 | 10.33 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN1 | 23.155808, 56.913509 | 2039 | Ground (GMT) |  | 1000 | 24/05/2026, 15:04 | 1 | 246 | 245 | 246 | 425 | 426 | 422 | [24 empty] | 185 mm² |  | 107 | 85 | 41 | 51 | 185 mm² |  | 205 | 297 | 212 | 52 | [8 empty] | Total Load R: 312; Total Load Y: 382; Total Load B: 253; Total Load N: 103 | 382 | 253 | 28.1198 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN1 | 23.155344, 56.910266 | 2009 | Pole (PMT) |  | 315 | 24/05/2026, 15:00 | 1 | 247 | 246 | 247 | 427 | 428 | 426 | 185 mm² |  | 33 | 20 | 15 | 19 | [38 empty] | Total Load R: 33; Total Load Y: 20; Total Load B: 15; Total Load N: 19 | 33 | 15 | 7.748 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN1 | 23.150354, 56.908828 | 4566 | Pole (PMT) |  | 100 | 24/05/2026, 14:56 | 1 | 246 | 247 | 246 | 427 | 426 | 428 | 185 mm² |  | 0 | 0 | 18 | 17 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 18; Total Load N: 17 | 18 | 0 | 13.3125 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN1 | 23.150354, 56.908828 | 1760 | Pole (PMT) |  | 100 | 24/05/2026, 14:52 | 1 | 242 | 244 | 244 | 420 | 422 | 422 | 120 mm² |  | 9 | 1 | 1 | 10 | 185 mm² |  | 42 | 63 | 74 | 27 | [32 empty] | Total Load R: 51; Total Load Y: 64; Total Load B: 75; Total Load N: 37 | 75 | 51 | 54.5596 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN1 | 23.145257, 56.897194 | 629 | Pole (PMT) |  | 200 | 24/05/2026, 14:45 | 1 | 243 | 243 | 242 | 421 | 419 | 420 | 120 mm² |  | 175 | 159 | 163 | 58 | [38 empty] | Total Load R: 175; Total Load Y: 159; Total Load B: 163; Total Load N: 58 | 175 | 159 | 63.8044 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN1 | 23.145257, 56.897194 | 628 | Pole (PMT) |  | 200 | 24/05/2026, 14:40 | 1 | 242 | 245 | 245 | 420 | 422 | 424 | 120 mm² |  | 166 | 95 | 113 | 56 | 120 mm² |  | 36 | 30 | 17 | 23 | [32 empty] | Total Load R: 202; Total Load Y: 125; Total Load B: 130; Total Load N: 79 | 202 | 125 | 73.4736 | Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN1 | 23.136573, 56.891915 | 2351 | Pole (PMT) |  | 200 | 24/05/2026, 14:34 | 1 | 246 | 247 | 247 | 427 | 426 | 429 | 185 mm² |  | 36 | 9 | 41 | 26 | [38 empty] | Total Load R: 36; Total Load Y: 9; Total Load B: 41; Total Load N: 26 | 41 | 9 | 15.1615 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN1 | 23.136573, 56.891915 | 630 | Pole (PMT) |  | 200 | 24/05/2026, 14:41 | 1 | 246 | 247 | 246 | 427 | 426 | 428 |  |  | 6 | 15 | 41 | 22 | 120 mm² |  | 28 | 26 | 9 | 9 | [32 empty] | Total Load R: 34; Total Load Y: 41; Total Load B: 50; Total Load N: 31 | 50 | 34 | 18.4896 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN1 | 23.136573, 56.891915 | 1834 | Pole (PMT) |  | 315 | 24/05/2026, 14:25 | 1 | 247 | 247 | 247 | 428 | 428 | 429 | [6 empty] | 185 mm² |  | 58 | 68 | 62 | 10 | [32 empty] | Total Load R: 58; Total Load Y: 68; Total Load B: 62; Total Load N: 10 | 68 | 58 | 16.003 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN4 | 23.08751, 56.819855 | 1537 | Ground (GMT) |  | 1000 | 24/05/2026, 14:16 | 1 | 241 | 242 | 243 | 418 | 418 | 420 | [24 empty] | 185 mm² |  | 75 | 50 | 78 | 44 |  |  | 0 | 0 | 0 | 0 | 185 mm² |  | 29 | 107 | 15 | 67 |  |  | Total Load R: 104; Total Load Y: 157; Total Load B: 93; Total Load N: 111 | 157 | 93 | 11.3668 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.135801, 56.891811 | 817 | Ground (GMT) |  | 1000 | 24/05/2026, 10:57 | 1 | 242 | 242 | 245 | 420 | 422 | 425 | 185 mm² |  | 15 | 18 | 15 | 16 | 185 mm² |  | 69 | 43 | 64 | 23 | 185 mm² |  | 72 | 100 | 133 | 54 | 185 mm² |  | 85 | 105 | 58 | 48 | [20 empty] | Total Load R: 241; Total Load Y: 266; Total Load B: 270; Total Load N: 141 | 270 | 241 | 19.6415 | OK - No Upgrade | OK - Balanced
Wadi Alain | AMLAH | K_LN4 | 23.129, 56.889793 | 809 | Ground (GMT) |  | 1000 | 24/05/2026, 10:49 | 1 | 242 | 243 | 245 | 421 | 423 | 426 | [18 empty] | 185 mm² |  | 77 | 50 | 44 | 30 | [6 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 98 | 40 | 56 | 56 | 185 mm² |  | 45 | 13 | 9 | 45 | 220 | 103 | 109 | 131 | 220 | 103 | 16.0423 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.128159, 56.889813 | 2038 | Ground (GMT) |  | 1000 | 24/05/2026, 10:42 | 1 | 248 | 251 | 250 | 430 | 433 | 437 | [24 empty] | 185 mm² |  | 13 | 8 | 1 | 12 | 185 mm² |  | 236 | 86 | 149 | 106 | 185 mm² |  | 121 | 125 | 144 | 106 | 185 mm² |  | 35 | 30 | 29 | 18 | 405 | 249 | 323 | 242 | 405 | 249 | 30.1637 | OK - No Upgrade | Need to Balance
Wadi Alain | AMLAH | K_LN4 | 23.126085, 56.889607 | 1712 | Ground (GMT) |  | 1000 | 24/05/2026, 10:23 | 1 | 242 | 244 | 242 | 424 | 421 | 423 | 185 mm² |  | 95 | 112 | 34 | 82 | 185 mm² |  | 131 | 126 | 97 | 54 | 185 mm² |  | 13 | 24 | 15 | 10 | 185 mm² |  | 11 | 1 | 1 | 13 | [20 empty] | Total Load R: 250; Total Load Y: 263; Total Load B: 147; Total Load N: 159 | 263 | 147 | 19.3144 | OK - No Upgrade | Need to Balance

## AL-EYNIN
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Feeder 9 | [5 empty] | Feeder 10 | [5 empty] | Feeder 11 | [5 empty] | Feeder 12 | [5 empty] | Feeder 13 | [5 empty] | Feeder 14 | [5 empty] | Feeder 15 | [5 empty] | Feeder 16 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Araqi | AL-EYNIN | K_LN05 | 23.29693, 56.542573 | 375 | Pole (PMT) | 3 | 315 | 07/06/2026, 13:33 | 1 | 240 | 238 | 238 | 417 | 413 | 410 | 185 mm² |  | 50 | 140 | 20 | 88 | 185 mm² |  | 80 | 60 | 65 | 25 | 120 mm² |  | 1 | 20 | 2 | 16 | [74 empty] | Total Load R: 131; Total Load Y: 220; Total Load B: 87; Total Load N: 129 | 220 | 87 | 50.4439 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.282681, 56.540676 | 386 | Ground (GMT) | 3 | 1000 | 05/06/2026, 09:05 | 1 | 237 | 279 | 240 | 411 | 416 | 413 | [12 empty] | 185 mm² |  | 75 | 59 | 74 | 15 | 185 mm² |  | 126 | 71 | 59 | 63 | 185 mm² |  | 101 | 107 | 92 | 14 | 185 mm² |  | 75 | 36 | 5 | 62 | [56 empty] | Total Load R: 377; Total Load Y: 273; Total Load B: 230; Total Load N: 154 | 377 | 230 | 26.8376 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.281756, 56.539615 | 387 | Pole (PMT) |  | 315 | 04/06/2026, 13:33 | 1 | 241 | 239 | 243 | 416 | 418 | 421 | 185 mm² |  | 19 | 35 | 27 | 13 | 185 mm² |  | 29 | 65 | 39 | 25 | [80 empty] | Total Load R: 48; Total Load Y: 100; Total Load B: 66; Total Load N: 38 | 100 | 48 | 22.8741 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.281186, 56.539537 | 387 | Pole (PMT) |  | 315 |  | 1 | [98 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL-EYNIN | K_LN04 | 23.281343, 56.537808 | 388 | Ground (GMT) |  | 1000 | 04/06/2026, 13:26 | 1 | 240 | 242 | 242 | 418 | 419 | 420 | 185 mm² |  | 61 | 41 | 77 | 35 | [6 empty] | 185 mm² |  | 12 | 6 | 50 | 39 | 120 mm² |  | 62 | 41 | 65 | 30 | 120 mm² |  | 35 | 3 | 145 | 135 | 120 mm² |  | 15 | 27 | 63 | 41 | 120 mm² |  | 19 | 85 | 56 | 47 | 185 mm² |  | 66 | 42 | 45 | 24 | [44 empty] | Total Load R: 270; Total Load Y: 245; Total Load B: 501; Total Load N: 351 | 501 | 245 | 36.2723 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.283744, 56.538803 | 397 | Ground (GMT) |  | 1000 | 04/06/2026, 13:17 | 1 | 240 | 243 | 244 | 420 | 423 | 419 | [12 empty] | 120 mm² |  | 48 | 15 | 11 | 37 | 185 mm² |  | 187 | 77 | 82 | 93 | 185 mm² |  | 139 | 91 | 126 | 60 | [62 empty] | Total Load R: 374; Total Load Y: 183; Total Load B: 219; Total Load N: 190 | 374 | 183 | 27.2071 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.279186, 56.534055 | 1549 | Pole (PMT) |  | 315 | 04/06/2026, 12:55 | 1 | 235 | 233 | 237 | 407 | 408 | 411 | 185 mm² |  | 47 | 82 | 59 | 21 | 185 mm² |  | 64 | 63 | 14 | 48 | [80 empty] | Total Load R: 111; Total Load Y: 145; Total Load B: 73; Total Load N: 69 | 145 | 73 | 32.4498 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.278927, 56.529442 | 04145 | Ground (GMT) |  | 500 | 04/06/2026, 12:51 | 1 | 241 | 240 | 243 | 417 | 419 | 417 | [36 empty] | 185 mm² |  | 39 | 46 | 62 | 20 | 185 mm² |  | 42 | 23 | 12 | 23 | [44 empty] | Total Load R: 81; Total Load Y: 69; Total Load B: 74; Total Load N: 43 | 81 | 69 | 11.7007 | OK - No Upgrade | OK - Balanced
Araqi | AL-EYNIN | K_LN04 | 23.281283, 56.531936 | 400 | Pole (PMT) |  | 315 | 04/06/2026, 12:41 | 1 | 240 | 241 | 242 | 415 | 417 | 422 | 185 mm² |  | 40 | 40 | 25 | 15 | 185 mm² |  | 61 | 79 | 60 | 20 | [80 empty] | Total Load R: 101; Total Load Y: 119; Total Load B: 85; Total Load N: 35 | 119 | 85 | 27.1547 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.283228, 56.531869 | 399 | Ground (GMT) |  | 1000 | 04/06/2026, 12:34 | 1 | 241 | 240 | 243 | 430 | 430 | 420 | [12 empty] | 185 mm² |  | 74 | 71 | 148 | 75 | 185 mm² |  | 45 | 29 | 80 | 44 | 185 mm² |  | 18 | 106 | 21 | 81 | 185 mm² |  | 30 | 31 | 46 | 17 | [56 empty] | Total Load R: 167; Total Load Y: 237; Total Load B: 295; Total Load N: 217 | 295 | 167 | 21.9711 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.283773, 56.534666 | 398 | Ground (GMT) |  | 1000 | 04/06/2026, 12:28 | 1 | 240 | 241 | 243 | 420 | 421 | 418 | 185 mm² |  | 31 | 10 | 11 | 23 | [6 empty] | 120 mm² |  | 44 | 85 | 52 | 47 | 120 mm² |  | 104 | 68 | 87 | 26 | 120 mm² |  | 16 | 1 | 1 | 13 | 120 mm² |  | 73 | 94 | 73 | 21 | 185 mm² |  | 37 | 28 | 34 | 11 | 185 mm² |  | 21 | 32 | 20 | 8 | [44 empty] | Total Load R: 326; Total Load Y: 318; Total Load B: 278; Total Load N: 149 | 326 | 278 | 23.7152 | OK - No Upgrade | OK - Balanced
Araqi | AL-EYNIN | K_LN04 | 23.286335, 56.538258 | 396 | Ground (GMT) |  | 1000 | 04/06/2026, 12:18 | 1 | 242 | 243 | 244 | 419 | 424 | 425 | 185 mm² |  | 53 | 12 | 29 | 32 | 185 mm² |  | 17 | 51 | 28 | 29 | 185 mm² |  | 22 | 1 | 36 | 26 | 185 mm² |  | 0 | 0 | 15 | 13 | [68 empty] | Total Load R: 92; Total Load Y: 64; Total Load B: 108; Total Load N: 100 | 108 | 64 | 7.8379 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.307391, 56.585589 | 395 | Ground (GMT) |  | 2000 | 04/06/2026, 12:14 | 1 | 241 | 243 | 244 | 420 | 425 | 420 | [18 empty] | 185 mm² |  | 0 | 1 | 0 | 1 | 120 mm² |  | 115 | 70 | 29 | 67 | 120 mm² |  | 81 | 80 | 65 | 20 | 120 mm² |  | 60 | 40 | 23 | 42 | 185 mm² |  | 56 | 56 | 37 | 24 | [6 empty] | 185 mm² |  | 26 | 52 | 38 | 19 | 185 mm² |  | 66 | 45 | 9 | 32 | 185 mm² |  | 62 | 46 | 80 | 46 | [18 empty] | 185 mm² |  | 62 | 114 | 116 | 74 | 528 | 504 | 397 | 325 | 528 | 397 | 19.205 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN03 | 23.280552, 56.552214 | 415 | Ground (GMT) |  | 1000 | 03/06/2026, 13:34 | 1 | 243 | 242 | 243 | 419 | 424 | 407 | [12 empty] | 185 mm² | [5 empty] | 185 mm² |  | 61 | 46 | 73 | 45 | 185 mm² |  | 65 | 92 | 93 | 21 | 185 mm² |  | 127 | 74 | 121 | 51 | 120 mm² |  | 93 | 45 | 106 | 48 | 185 mm² |  | 82 | 128 | 167 | 73 | [44 empty] | Total Load R: 428; Total Load Y: 385; Total Load B: 560; Total Load N: 238 | 560 | 385 | 40.6408 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN03 | 23.280939, 56.559783 | 1277 | Pole (PMT) |  | 315 | 03/06/2026, 13:26 | 1 | 246 | 244 | 246 | 424 | 429 | 425 | 185 mm² |  | 42 | 49 | 39 | 12 | [86 empty] | Total Load R: 42; Total Load Y: 49; Total Load B: 39; Total Load N: 12 | 49 | 39 | 11.4238 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN03 | 23.279666, 56.562528 | 1449 | Pole (PMT) |  | 315 | 03/06/2026, 13:19 | 1 | 244 | 243 | 246 | 422 | 428 | 423 | 185 mm² |  | 63 | 48 | 22 | 39 | 240 mm² |  | 54 | 45 | 69 | 20 | [80 empty] | Total Load R: 117; Total Load Y: 93; Total Load B: 91; Total Load N: 59 | 117 | 91 | 27.1487 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN03 | 23.281884, 56.562589 | 1491 | Pole (PMT) |  | 315 | 03/06/2026, 13:14 | 1 | 246 | 244 | 247 | 424 | 430 | 426 | 120 mm² |  | 19 | 25 | 13 | 9 | 185 mm² |  | 32 | 39 | 53 | 22 | [80 empty] | Total Load R: 51; Total Load Y: 64; Total Load B: 66; Total Load N: 31 | 66 | 51 | 15.3872 | OK - No Upgrade | OK - Balanced
Araqi | AL-EYNIN | K_LN03 | 23.280446, 56.567352 | 1563 | Pole (PMT) |  | 315 | 03/06/2026, 13:07 | 1 | 245 | 245 | 247 | 423 | 430 | 427 | 185 mm² |  | 100 | 31 | 27 | 39 | 120 mm² |  | 29 | 11 | 26 | 16 | [80 empty] | Total Load R: 129; Total Load Y: 42; Total Load B: 53; Total Load N: 55 | 129 | 42 | 30.0041 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN06 | 23.308061, 56.586232 | 356 | Ground (GMT) |  | 500 | 02/06/2026, 21:50 | 1 | 244 | 244 | 246 | 418 | 427 | 441 | 185 mm² |  | 114 | 138 | 128 | 57 | 185 mm² |  | 140 | 102 | 100 | 85 | 185 mm² |  | 0 | 0 | 0 | 0 | [74 empty] | Total Load R: 254; Total Load Y: 240; Total Load B: 228; Total Load N: 142 | 254 | 228 | 36.7791 | OK - No Upgrade | OK - Balanced
Araqi | AL-EYNIN | K_LN06 | 23.308061, 56.58623 | 1746 | Ground (GMT) |  | 1000 | 02/06/2026, 21:49 | 1 | 246 | 244 | 244 | 425 | 425 | 421 | 185 mm² |  | 156 | 162 | 147 | 31 | 185 mm² |  | 174 | 122 | 144 | 51 | [80 empty] | Total Load R: 330; Total Load Y: 284; Total Load B: 291; Total Load N: 82 | 330 | 284 | 24.292 | OK - No Upgrade | OK - Balanced
Araqi | AL-EYNIN | K_LN06 | 23.308061, 56.586232 | 358 | Ground (GMT) |  | 500 | 02/06/2026, 21:47 | 1 | 245 | 244 | 247 | 423 | 428 | 427 | 185 mm² |  | 31 | 55 | 33 | 96 | 185 mm² |  | 106 | 106 | 85 | 100 | [80 empty] | Total Load R: 137; Total Load Y: 161; Total Load B: 118; Total Load N: 196 | 161 | 118 | 23.5916 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN05 | 23.308062, 56.586227 | 406 | Ground (GMT) |  | 1000 | 02/06/2026, 21:46 | 1 | 244 | 244 | 246 | 422 | 425 | 426 | 185 mm² |  | 150 | 171 | 165 | 40 |  |  | 77 | 124 | 70 | 48 | [80 empty] | Total Load R: 227; Total Load Y: 295; Total Load B: 235; Total Load N: 88 | 295 | 227 | 21.5623 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN03 |  | 364 | Ground (GMT) |  | 500 | 02/06/2026, 21:45 | 1 | 245 | 244 | 247 | 422 | 430 | 426 | 185 mm² |  | 133 | 123 | 76 | 116 | 185 mm² |  | 101 | 130 | 97 | 119 | [80 empty] | Total Load R: 234; Total Load Y: 253; Total Load B: 173; Total Load N: 235 | 253 | 173 | 36.9848 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN02 |  | 367 | Ground (GMT) |  | 1000 | 02/06/2026, 21:43 | 1 | 232 | 233 | 235 | 404 | 404 | 408 | 185 mm² |  | 190 | 96 | 100 | 85 | 185 mm² |  | 155 | 119 | 101 | 55 | [80 empty] | Total Load R: 345; Total Load Y: 215; Total Load B: 201; Total Load N: 140 | 345 | 201 | 24.1413 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN02 |  | 366 | Ground (GMT) |  | 1000 | 02/06/2026, 21:41 | 1 | 241 | 240 | 246 | 426 | 420 | 416 | [6 empty] | 185 mm² |  | 81 | 75 | 90 | 85 | 185 mm² |  | 170 | 211 | 202 | 100 |  |  | 20 | 34 | 30 | 17 | [68 empty] | Total Load R: 271; Total Load Y: 320; Total Load B: 322; Total Load N: 202 | 322 | 271 | 23.7589 | OK - No Upgrade | OK - Balanced
Araqi | AL-EYNIN | K_LN03 | 23.281598, 56.556285 | 414 | Ground (GMT) |  | 1000 | 02/06/2026, 13:37 | 1 | 244 | 243 | 245 | 422 | 427 | 426 | [24 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 34 | 53 | 51 | 30 | 185 mm² |  | 69 | 88 | 71 | 20 | 185 mm² |  | 4 | 10 | 26 | 8 | [44 empty] | Total Load R: 107; Total Load Y: 151; Total Load B: 148; Total Load N: 58 | 151 | 107 | 11.037 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN03 |  | 413 | Pole (PMT) |  | 315 | 02/06/2026, 13:29 | 1 | 244 | 244 | 247 | 423 | 427 | 425 | 120 mm² |  | 42 | 16 | 20 | 17 | [86 empty] | Total Load R: 42; Total Load Y: 16; Total Load B: 20; Total Load N: 17 | 42 | 16 | 9.7688 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN03 | 23.286448, 56.555877 | 2100 | Pole (PMT) |  | 315 | 02/06/2026, 13:24 | 1 | 245 | 244 | 246 | 424 | 429 | 427 | 185 mm² |  | 23 | 17 | 15 | 11 | [86 empty] | Total Load R: 23; Total Load Y: 17; Total Load B: 15; Total Load N: 11 | 23 | 15 | 5.3622 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN03 | 23.28469, 56.554315 | 412 | Pole (PMT) |  | 100 | 02/06/2026, 13:19 | 1 | 227 | 223 | 235 | 409 | 409 | 407 | 120 mm² |  | 35 | 6 | 28 | 22 | [86 empty] | Total Load R: 35; Total Load Y: 6; Total Load B: 28; Total Load N: 22 | 35 | 6 | 24.7943 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN03 | 23.291214, 56.556574 | 365 | Pole (PMT) |  | 315 | 02/06/2026, 13:12 | 1 | 246 | 246 | 248 | 425 | 431 | 429 | 185 mm² |  | 35 | 7 | 10 | 25 | [86 empty] | Total Load R: 35; Total Load Y: 7; Total Load B: 10; Total Load N: 25 | 35 | 7 | 8.1791 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN06 | 23.27942, 56.545498 | 1424 | Ground (GMT) |  | 1000 | 30/05/2026, 12:49 | 1 | 243 | 242 | 245 | 421 | 422 | 426 | 185 mm² |  | 118 | 144 | 107 | 39 | 185 mm² |  | 37 | 6 | 20 | 21 | 185 mm² |  | 59 | 118 | 53 | 52 | 185 mm² |  | 109 | 81 | 102 | 27 | 185 mm² |  | 118 | 129 | 118 | 34 | [62 empty] | Total Load R: 441; Total Load Y: 478; Total Load B: 400; Total Load N: 173 | 478 | 400 | 34.8554 | OK - No Upgrade | OK - Balanced
Araqi | AL-EYNIN | K_LN06 | 23.281278, 56.547522 | 354 | Ground (GMT) |  | 1000 | 30/05/2026, 12:31 | 1 | 243 | 245 | 243 | 425 | 425 | 420 | 120 mm² |  | 59 | 87 | 45 | 43 | 185 mm² |  | 48 | 26 | 34 | 19 | 120 mm² |  | 14 | 13 | 8 | 4 | 185 mm² |  | 59 | 39 | 38 | 31 | [68 empty] | Total Load R: 180; Total Load Y: 165; Total Load B: 125; Total Load N: 97 | 180 | 125 | 13.2502 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN06 | 23.288994, 56.551511 | 1921 | Ground (GMT) |  | 1000 | 30/05/2026, 12:22 | 1 | 245 | 246 | 248 | 427 | 428 | 431 | [6 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 23 | 77 | 22 | 54 | 185 mm² |  | 117 | 78 | 129 | 59 | [68 empty] | Total Load R: 140; Total Load Y: 155; Total Load B: 151; Total Load N: 113 | 155 | 140 | 11.4636 | OK - No Upgrade | OK - Balanced
Araqi | AL-EYNIN | K_LN06 | 23.280661, 56.546386 | 355 | Ground (GMT) |  | 1000 | 29/05/2026, 12:44 | 1 | 246 | 245 | 248 | 424 | 428 | 430 | 185 mm² |  | 45 | 17 | 62 | 33 | 185 mm² |  | 33 | 60 | 92 | 51 | 185 mm² |  | 35 | 4 | 36 | 40 | 120 mm² |  | 97 | 41 | 5 | 80 | 120 mm² |  | 65 | 51 | 77 | 24 | 185 mm² |  | 131 | 40 | 39 | 90 | 120 mm² |  | 27 | 76 | 62 | 44 | 185 mm² |  | 20 | 36 | 2 | 30 | [44 empty] | Total Load R: 453; Total Load Y: 325; Total Load B: 375; Total Load N: 392 | 453 | 325 | 33.2678 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN06 | 23.278053, 56.545716 | 357 | Ground (GMT) |  | 1000 | 29/05/2026, 12:35 | 1 | 246 | 250 | 254 | 421 | 431 | 438 | 185 mm² |  | 95 | 57 | 52 | 17 | 185 mm² |  | 89 | 5 | 40 | 84 | 120 mm² |  | 33 | 5 | 13 | 25 | 185 mm² |  | 28 | 27 | 20 | 7 | 185 mm² |  | 17 | 12 | 0 | 19 | 185 mm² |  | 58 | 91 | 120 | 37 | 185 mm² |  | 40 | 55 | 84 | 43 | 185 mm² |  | 76 | 75 | 75 | 12 | [44 empty] | Total Load R: 436; Total Load Y: 327; Total Load B: 404; Total Load N: 244 | 436 | 327 | 31.7928 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN06 | 23.279146, 56.545448 | 1848 | Ground (GMT) |  | 1000 | 29/05/2026, 12:26 | 1 | 248 | 246 | 250 | 428 | 431 | 434 | [12 empty] | 185 mm² |  | 81 | 95 | 28 | 37 | 185 mm² |  | 57 | 130 | 95 | 65 | 185 mm² |  | 104 | 72 | 21 | 55 | [62 empty] | Total Load R: 242; Total Load Y: 297; Total Load B: 144; Total Load N: 157 | 297 | 144 | 22.0171 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN01 | 23.285267, 56.553863 | 2303 | Ground (GMT) |  | 1000 | 28/05/2026, 14:37 | 1 | 243 | 242 | 246 | 424 | 422 | 424 | 185 mm² |  | 135 | 110 | 136 | 52 | 185 mm² |  | 132 | 3 | 53 | 23 | 185 mm² |  | 118 | 50 | 30 | 60 | 185 mm² |  | 7 | 4 | 28 | 28 | 185 mm² |  | 50 | 61 | 30 | 30 | 185 mm² |  | 0 | 0 | 0 | 0 | [56 empty] | Total Load R: 442; Total Load Y: 228; Total Load B: 277; Total Load N: 193 | 442 | 228 | 32.46 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.296927, 56.54955 | 2115 | Pole (PMT) |  | 315 | 28/05/2026, 14:34 | 1 | 239 | 242 | 243 | 418 | 418 | 422 | 185 mm² |  | 74 | 30 | 33 | 33 | 185 mm² |  | 111 | 102 | 83 | 29 | [80 empty] | Total Load R: 185; Total Load Y: 132; Total Load B: 116; Total Load N: 62 | 185 | 116 | 42.5205 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.294385, 56.546889 | 4265 | Ground (GMT) |  | 1000 | 28/05/2026, 14:30 | 1 | 241 | 243 | 244 | 420 | 422 | 423 | [36 empty] | 185 mm² |  | 35 | 77 | 55 | 37 | 185 mm² |  | 170 | 158 | 155 | 27 | [44 empty] | Total Load R: 205; Total Load Y: 235; Total Load B: 210; Total Load N: 64 | 235 | 205 | 17.0953 | OK - No Upgrade | OK - Balanced
Araqi | AL-EYNIN | K_LN01 | 23.283246, 56.552649 | 417 | Ground (GMT) |  | 1000 | 28/05/2026, 14:31 | 1 | 242 | 245 | 243 | 423 | 419 | 422 | [6 empty] | 185 mm² |  | 105 | 49 | 20 | 50 | 185 mm² |  | 60 | 57 | 67 | 35 | 185 mm² |  | 100 | 150 | 244 | 70 | 185 mm² |  | 80 | 13 | 30 | 35 | 185 mm² |  | 100 | 85 | 156 | 77 | [6 empty] | 185 mm² |  | 115 | 100 | 100 | 40 | [44 empty] | Total Load R: 560; Total Load Y: 454; Total Load B: 617; Total Load N: 307 | 617 | 454 | 45.205 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN01 | 23.282776, 56.551069 | 360 | Ground (GMT) |  | 1000 | 28/05/2026, 14:25 | 1 | 243 | 241 | 243 | 423 | 420 | 424 | 185 mm² |  | 40 | 120 | 63 | 70 | 185 mm² |  | 30 | 10 | 33 | 30 | 185 mm² |  | 100 | 100 | 223 | 100 | 185 mm² |  | 90 | 30 | 50 | 50 | 185 mm² |  | 40 | 30 | 13 | 15 | 185 mm² |  | 30 | 5 | 10 | 15 | 185 mm² |  | 40 | 30 | 50 | 25 | 185 mm² |  | 60 | 65 | 60 | 30 | [44 empty] | Total Load R: 430; Total Load Y: 390; Total Load B: 502; Total Load N: 335 | 502 | 390 | 36.7794 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.291768, 56.548078 | 1231 | Ground (GMT) |  | 1000 | 28/05/2026, 14:23 | 1 | 243 | 242 | 244 | 420 | 425 | 422 | [12 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 44 | 58 | 28 | 27 | 185 mm² |  | 30 | 11 | 32 | 20 | 185 mm² |  | 42 | 25 | 41 | 17 |  |  | 131 | 81 | 125 | 47 | [50 empty] | Total Load R: 247; Total Load Y: 175; Total Load B: 226; Total Load N: 111 | 247 | 175 | 17.9683 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN01 | 23.279123, 56.550393 | 427 | Ground (GMT) |  | 1000 | 28/05/2026, 14:18 | 1 | 242 | 246 | 244 | 421 | 422 | 426 | 120 mm² |  | 100 | 7 | 77 | 93 | [6 empty] | 120 mm² |  | 76 | 50 | 83 | 40 | 185 mm² |  | 33 | 20 | 42 | 15 | 185 mm² |  | 20 | 35 | 37 | 20 | 185 mm² |  | 70 | 60 | 50 | 40 | 120 mm² |  | 70 | 60 | 50 | 30 | 120 mm² |  | 100 | 120 | 70 | 60 | [44 empty] | Total Load R: 469; Total Load Y: 352; Total Load B: 409; Total Load N: 298 | 469 | 352 | 34.1992 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.28979, 56.542203 | 1230 | Ground (GMT) |  | 1000 | 28/05/2026, 14:17 | 1 | 243 | 242 | 244 | 421 | 424 | 423 | [24 empty] | 185 mm² |  | 10 | 0 | 1 | 10 | 185 mm² |  | 128 | 91 | 78 | 32 | 185 mm² |  | 24 | 12 | 64 | 46 | 185 mm² |  | 59 | 52 | 38 | 22 | [44 empty] | Total Load R: 221; Total Load Y: 155; Total Load B: 181; Total Load N: 110 | 221 | 155 | 16.1152 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN01 | 23.277978, 56.548747 | 1719 | Ground (GMT) |  | 1000 | 28/05/2026, 14:12 | 1 | 240 | 243 | 242 | 417 | 420 | 423 | 185 mm² |  | 9 | 0 | 14 | 14 | 70 mm² |  | 0 | 0 | 0 | 0 | 240 mm² |  | 40 | 16 | 25 | 10 | 185 mm² |  | 80 | 70 | 60 | 40 | 185 mm² |  | 50 | 8 | 40 | 21 | 185 mm² |  | 25 | 16 | 36 | 25 | 185 mm² |  | 31 | 62 | 63 | 24 | [50 empty] | Total Load R: 235; Total Load Y: 172; Total Load B: 238; Total Load N: 134 | 238 | 172 | 17.1899 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN01 | 23.276411, 56.547026 | 362 | Pole (PMT) |  | 315 | 28/05/2026, 14:06 | 1 | 241 | 244 | 243 | 420 | 419 | 421 | 185 mm² |  | 1 | 3 | 0 | 5 | 185 mm² |  | 30 | 3 | 0 | 22 | [80 empty] | Total Load R: 31; Total Load Y: 6; Total Load B: 0; Total Load N: 27 | 31 | 0 | 7.1591 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.288545, 56.547084 | 382 | Ground (GMT) |  | 1000 | 28/05/2026, 14:09 | 1 | 239 | 237 | 240 | 413 | 416 | 413 | 120 mm² | [5 empty] | 120 mm² |  | 96 | 97 | 95 | 17 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 140 | 145 | 81 | 53 | 120 mm² |  | 86 | 63 | 52 | 24 | 120 mm² |  | 42 | 89 | 170 | 103 | 120 mm² |  | 21 | 45 | 34 | 18 | 240 mm² |  | 23 | 173 | 87 | 68 | [44 empty] | Total Load R: 408; Total Load Y: 612; Total Load B: 519; Total Load N: 283 | 612 | 408 | 43.7786 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN01 | 23.273864, 56.543552 | 1866 | Ground (GMT) |  | 1000 | 28/05/2026, 14:00 | 1 | 242 | 244 | 243 | 421 | 420 | 426 | [18 empty] | 185 mm² |  | 9 | 10 | 22 | 12 | 120 mm² |  | 4 | 0 | 0 | 4 | 120 mm² |  | 1 | 1 | 0 | 1 | 120 mm² |  | 0 | 0 | 0 | 0 | [50 empty] | Total Load R: 14; Total Load Y: 11; Total Load B: 22; Total Load N: 17 | 22 | 11 | 1.6042 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.286145, 56.545453 | 385 | Pole (PMT) |  | 315 | 28/05/2026, 13:56 | 1 | 236 | 240 | 239 | 413 | 414 | 411 | 120 mm² |  | 193 | 83 | 178 | 116 | [86 empty] | Total Load R: 193; Total Load Y: 83; Total Load B: 178; Total Load N: 116 | 193 | 83 | 43.8286 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN01 | 23.275627, 56.545418 | 363 | Ground (GMT) |  | 1000 | 28/05/2026, 13:55 | 1 | 239 | 243 | 241 | 417 | 416 | 420 | [6 empty] | 185 mm² |  | 100 | 50 | 90 | 47 | 185 mm² |  | 140 | 160 | 135 | 90 | 185 mm² |  | 40 | 125 | 40 | 77 | [6 empty] | 120 mm² |  | 90 | 60 | 80 | 50 | 120 mm² |  | 170 | 118 | 122 | 50 | 120 mm² |  | 45 | 63 | 48 | 43 | [44 empty] | Total Load R: 585; Total Load Y: 576; Total Load B: 515; Total Load N: 357 | 585 | 515 | 42.2525 | OK - No Upgrade | OK - Balanced
Araqi | AL-EYNIN | K_LN04 | 23.288338, 56.545706 | 1395 | Pole (PMT) |  | 315 | 28/05/2026, 13:52 | 1 | 238 | 240 | 242 | 415 | 416 | 420 | 120 mm² |  | 78 | 46 | 46 | 28 | 120 mm² |  | 117 | 103 | 78 | 38 | [80 empty] | Total Load R: 195; Total Load Y: 149; Total Load B: 124; Total Load N: 66 | 195 | 124 | 44.4972 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN01 | 23.279039, 56.548359 | 361 | Ground (GMT) |  | 1000 | 28/05/2026, 13:48 | 1 | 240 | 241 | 243 | 413 | 421 | 416 | [6 empty] | 185 mm² |  | 53 | 26 | 30 | 23 | 185 mm² |  | 85 | 73 | 40 | 20 | 185 mm² |  | 114 | 85 | 100 | 25 | 185 mm² |  | 0 | 11 | 3 | 8 | 185 mm² |  | 190 | 130 | 70 | 111 | 185 mm² |  | 100 | 130 | 50 | 30 | 185 mm² |  | 70 | 30 | 60 | 150 | [44 empty] | Total Load R: 612; Total Load Y: 485; Total Load B: 353; Total Load N: 367 | 612 | 353 | 43.7786 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN04 | 23.286182, 56.545343 | 385 | Pole (PMT) |  | 200 | 28/05/2026, 18:47 | 1 | 238 | 241 | 239 | 416 | 414 | 415 | 120 mm² |  | 130 | 71 | 179 | 102 | [86 empty] | Total Load R: 130; Total Load Y: 71; Total Load B: 179; Total Load N: 102 | 179 | 71 | 64.4877 | OK - No Upgrade | Need to Balance
Araqi | AL-EYNIN | K_LN01 | 23.281497, 56.550187 | 4342 | Ground (GMT) |  | 1000 | 28/05/2026, 13:41 | 1 | 242 | 244 | 243 | 421 | 420 | 425 | [12 empty] | 240 mm² |  | 245 | 230 | 208 | 50 | 185 mm² |  | 25 | 20 | 30 | 12 | 185 mm² |  | 1 | 1 | 0 | 2 | [62 empty] | Total Load R: 271; Total Load Y: 251; Total Load B: 238; Total Load N: 64 | 271 | 238 | 19.7611 | OK - No Upgrade | OK - Balanced
Araqi | AL-EYNIN | K_LN04 | 23.28606, 56.545543 | 380 | Pole (PMT) |  | 315 |  | 1 | [98 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL-EYNIN | K_LN01 | 23.286918, 56.548494 | 353 | Pole (PMT) |  | 315 | 28/05/2026, 13:33 | 1 | 238 | 237 | 236 | 413 | 409 | 412 | 120 mm² |  | 66 | 40 | 50 | 25 | 185 mm² |  | 25 | 60 | 50 | 15 | [80 empty] | Total Load R: 91; Total Load Y: 100; Total Load B: 100; Total Load N: 40 | 100 | 91 | 22.7091 | OK - No Upgrade | OK - Balanced
Araqi | AL-EYNIN | K_LN01 | 23.289831, 56.550157 | 351 | Ground (GMT) |  | 1000 | 28/05/2026, 13:25 | 1 | 247 | 243 | 246 | 422 | 428 | 424 | 185 mm² |  | 106 | 85 | 113 | 24 | 185 mm² |  | 5 | 0 | 0 | 5 | [80 empty] | Total Load R: 111; Total Load Y: 85; Total Load B: 113; Total Load N: 29 | 113 | 85 | 8.2595 | OK - No Upgrade | OK - Balanced
Araqi | AL-EYNIN | K_LN02 | 23.309125, 56.586657 | 530 | Ground (GMT) |  | 1000 | 25/05/2026, 11:22 | 1 | 244 | 244 | 245 | 421 | 426 | 425 | 185 mm² | [5 empty] | 185 mm² |  | 29 | 63 | 33 | 26 | [18 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | [56 empty] | Total Load R: 29; Total Load Y: 63; Total Load B: 33; Total Load N: 26 | 63 | 29 | 4.5939 | OK - No Upgrade | Need to Balance

## KUBARAH
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Wadi Alain | KUBARAH | K_LN4 | 23.025778, 56.851929 | 769 | Pole (PMT) | 5 | 100 | 11/06/2026, 16:15 | 1 | 256 | 260 | 258 | 449 | 449 | 451 | 120 mm² |  | 23 | 26 | 27 | 15 | 120 mm² |  | 12 | 25 | 26 | 17 | [32 empty] | Total Load R: 35; Total Load Y: 51; Total Load B: 53; Total Load N: 32 | 53 | 35 | 41.2176 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.025772, 56.851926 | 00768 | Pole (PMT) | 3 | 100 | 11/06/2026, 16:13 | 1 | 243 | 247 | 245 | 427 | 425 | 428 | 120 mm² |  | 16 | 9 | 7 | 10 | [38 empty] | Total Load R: 16; Total Load Y: 9; Total Load B: 7; Total Load N: 10 | 16 | 7 | 11.8334 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.019, 56.849245 | 768 | Pole (PMT) | 3 | 100 | 11/06/2026, 16:08 | 1 | 237 | 241 | 237 | 415 | 411 | 417 | 120 mm² |  | 35 | 31 | 48 | 42 | [38 empty] | Total Load R: 35; Total Load Y: 31; Total Load B: 48; Total Load N: 42 | 48 | 31 | 34.5025 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.010292, 56.846782 | 771 | Pole (PMT) | 3 | 100 | 11/06/2026, 16:07 | 1 | 246 | 246 | 244 | 424 | 423 | 424 | 120 mm² |  | 62 | 32 | 36 | 33 | [38 empty] | Total Load R: 62; Total Load Y: 32; Total Load B: 36; Total Load N: 33 | 62 | 32 | 45.5322 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.003944, 56.844669 | 770 | Pole (PMT) | 3 | 100 | 11/06/2026, 16:06 | 1 | 244 | 247 | 245 | 429 | 426 | 429 | 120 mm² |  | 10 | 9 | 9 | 8 | [38 empty] | Total Load R: 10; Total Load Y: 9; Total Load B: 9; Total Load N: 8 | 10 | 9 | 7.4305 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN4 | 22.966634, 56.856961 | 767 | Pole (PMT) | 3 | 315 | 11/06/2026, 15:44 | 1 | 243 | 245 | 244 | 427 | 423 | 426 | 120 mm² |  | 50 | 67 | 34 | 43 | [38 empty] | Total Load R: 50; Total Load Y: 67; Total Load B: 34; Total Load N: 43 | 67 | 34 | 15.7309 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.022466, 56.828566 | 1745 | Pole (PMT) | 3 | 100 | 11/06/2026, 15:12 | 1 | 247 | 250 | 248 | 433 | 430 | 434 | 120 mm² |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN4 | 23.015568, 56.836535 | 766 | Pole (PMT) | 3 | 315 | 11/06/2026, 15:06 | 1 | 246 | 248 | 247 | 430 | 428 | 433 | 120 mm² |  | 66 | 84 | 97 | 30 | [38 empty] | Total Load R: 66; Total Load Y: 84; Total Load B: 97; Total Load N: 30 | 97 | 66 | 22.9346 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.04609, 56.850768 | 763 | Pole (PMT) | 0 | 50 | 11/06/2026, 14:57 | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN4 | 23.046045, 56.85078 | 50 | Pole (PMT) |  | 50 |  | 1 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN4 | 23.049699, 56.851092 | 4544 | Pole (PMT) | 3 | 100 | 11/06/2026, 14:50 | 1 | 250 | 252 | 251 | 437 | 436 | 438 | 120 mm² |  | 11 | 9 | 7 | 12 | [38 empty] | Total Load R: 11; Total Load Y: 9; Total Load B: 7; Total Load N: 12 | 11 | 7 | 8.326 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.054845, 56.845145 | 762 | Pole (PMT) | 5 | 315 | 11/06/2026, 14:46 | 1 | 250 | 251 | 252 | 436 | 437 | 436 | 120 mm² |  | 74 | 139 | 57 | 92 | [38 empty] | Total Load R: 74; Total Load Y: 139; Total Load B: 57; Total Load N: 92 | 139 | 57 | 33.3236 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.054154, 56.835935 | 4752 | Pole (PMT) | 3 | 100 | 11/06/2026, 14:39 | 1 | 251 | 253 | 253 | 440 | 440 | 442 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN4 | 23.058718, 56.840077 | 4776 | Pole (PMT) | 3 | 100 | 11/06/2026, 14:34 | 1 | 250 | 254 | 251 | 438 | 436 | 438 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN4 | 23.061707, 56.837618 | 759 | Pole (PMT) | 5 | 315 | 11/06/2026, 14:30 | 1 | 250 | 251 | 240 | 436 | 422 | 415 | 120 mm² |  | 79 | 59 | 67 | 17 | [38 empty] | Total Load R: 79; Total Load Y: 59; Total Load B: 67; Total Load N: 17 | 79 | 59 | 18.9393 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.073174, 56.827774 | 1835 | Pole (PMT) | 3 | 315 | 11/06/2026, 14:23 | 1 | 249 | 253 | 250 | 435 | 433 | 438 | 120 mm² |  | 51 | 46 | 28 | 46 | 120 mm² |  | 33 | 22 | 77 | 33 | [32 empty] | Total Load R: 84; Total Load Y: 68; Total Load B: 105; Total Load N: 79 | 105 | 68 | 25.1147 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.05598, 56.818854 | 760 | Pole (PMT) | 3 | 315 | 11/06/2026, 14:16 | 1 | 251 | 249 | 252 | 427 | 430 | 437 | 120 mm² |  | 21 | 51 | 14 | 33 | 120 mm² |  | 48 | 59 | 63 | 13 | [32 empty] | Total Load R: 69; Total Load Y: 110; Total Load B: 77; Total Load N: 46 | 110 | 69 | 25.8268 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.072752, 56.812397 | 4766 | Pole (PMT) | 3 | 100 | 11/06/2026, 14:06 | 1 | 252 | 254 | 254 | 440 | 441 | 442 | 120 mm² |  | 7 | 6 | 5 | 5 | [38 empty] | Total Load R: 7; Total Load Y: 6; Total Load B: 5; Total Load N: 5 | 7 | 5 | 5.3347 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.062768, 56.814439 | 761 | Pole (PMT) | 3 | 100 | 11/06/2026, 13:55 | 1 | 248 | 251 | 250 | 430 | 435 | 436 | 120 mm² |  | 27 | 24 | 20 | 18 | [38 empty] | Total Load R: 27; Total Load Y: 24; Total Load B: 20; Total Load N: 18 | 27 | 20 | 20.1091 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.076894, 56.821367 | 758 | Pole (PMT) | 3 | 100 | 11/06/2026, 13:49 | 1 | 242 | 243 | 242 | 426 | 427 | 429 | 120 mm² |  | 100 | 94 | 84 | 17 | [38 empty] | Total Load R: 100; Total Load Y: 94; Total Load B: 84; Total Load N: 17 | 100 | 84 | 73.7854 | Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN4 | 23.089016, 56.812584 | 1780 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:45 | 1 | 245 | 247 | 248 | 427 | 432 | 429 | 120 mm² |  | 31 | 27 | 37 | 12 | [38 empty] | Total Load R: 31; Total Load Y: 27; Total Load B: 37; Total Load N: 12 | 37 | 27 | 27.3647 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.088995, 56.812562 | 834 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:44 | 1 | 245 | 248 | 248 | 427 | 434 | 431 | 120 mm² |  | 25 | 20 | 28 | 15 | [38 empty] | Total Load R: 25; Total Load Y: 20; Total Load B: 28; Total Load N: 15 | 28 | 20 | 20.7084 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.088991, 56.812559 | 833 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:42 | 1 | 246 | 246 | 249 | 429 | 433 | 432 | 50 mm² |  | 15 | 15 | 15 | 8 | [38 empty] | Total Load R: 15; Total Load Y: 15; Total Load B: 15; Total Load N: 8 | 15 | 15 | 11.1457 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN4 | 23.088994, 56.812563 | 832 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:41 | 1 | 246 | 248 | 249 | 428 | 434 | 433 | 120 mm² |  | 32 | 25 | 26 | 15 | [38 empty] | Total Load R: 32; Total Load Y: 25; Total Load B: 26; Total Load N: 15 | 32 | 25 | 23.7222 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.089015, 56.812581 | 831 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:40 | 1 | 246 | 248 | 249 | 429 | 432 | 432 | 120 mm² |  | 10 | 9 | 7 | 9 | [38 empty] | Total Load R: 10; Total Load Y: 9; Total Load B: 7; Total Load N: 9 | 10 | 7 | 7.4305 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.089002, 56.81257 | 4491 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:39 | 1 | 247 | 249 | 248 | 430 | 436 | 433 | 120 mm² |  | 10 | 11 | 10 | 12 | [38 empty] | Total Load R: 10; Total Load Y: 11; Total Load B: 10; Total Load N: 12 | 11 | 10 | 8.1926 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN4 | 23.089023, 56.812588 | 830 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:38 | 1 | 245 | 248 | 249 | 426 | 432 | 433 | 120 mm² |  | 28 | 10 | 11 | 15 | [38 empty] | Total Load R: 28; Total Load Y: 10; Total Load B: 11; Total Load N: 15 | 28 | 10 | 20.6599 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.088989, 56.812555 | 842 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:37 | 1 | 244 | 245 | 245 | 420 | 421 | 422 | 120 mm² |  | 15 | 15 | 16 | 10 | [38 empty] | Total Load R: 15; Total Load Y: 15; Total Load B: 16; Total Load N: 10 | 16 | 15 | 11.6394 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN4 | 23.088996, 56.812565 | 4673 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:36 | 1 | 246 | 247 | 247 | 425 | 424 | 424 | 120 mm² |  | 5 | 5 | 4 | 5 | [38 empty] | Total Load R: 5; Total Load Y: 5; Total Load B: 4; Total Load N: 5 | 5 | 4 | 3.6806 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN4 | 23.08901, 56.812578 | 841 | Pole (PMT) | 5 | 100 | 10/06/2026, 18:35 | 1 | 259 | 258 | 259 | 445 | 444 | 445 | 120 mm² |  | 27 | 24 | 29 | 15 | 120 mm² |  | 10 | 26 | 11 | 16 | [32 empty] | Total Load R: 37; Total Load Y: 50; Total Load B: 40; Total Load N: 31 | 50 | 37 | 38.5381 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.088989, 56.812556 | 0840 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:33 | 1 | 243 | 249 | 249 | 431 | 434 | 432 | 50 mm² |  | 7 | 5 | 5 | 6 | [38 empty] | Total Load R: 7; Total Load Y: 5; Total Load B: 5; Total Load N: 6 | 7 | 5 | 5.2256 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.089022, 56.812587 | 840 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:31 | 1 | 245 | 243 | 242 | 425 | 426 | 425 | 120 mm² |  | 10 | 8 | 8 | 7 | [38 empty] | Total Load R: 10; Total Load Y: 8; Total Load B: 8; Total Load N: 7 | 10 | 8 | 7.3612 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.089024, 56.812588 | 839 | Pole (PMT) | 4 | 100 | 10/06/2026, 18:30 | 1 | 245 | 249 | 250 | 430 | 436 | 432 | 120 mm² |  | 31 | 33 | 23 | 21 | [38 empty] | Total Load R: 31; Total Load Y: 33; Total Load B: 23; Total Load N: 21 | 33 | 23 | 24.5778 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.08899, 56.812558 | 838 | Pole (PMT) | 3 | 200 | 10/06/2026, 18:29 | 1 | 245 | 247 | 248 | 429 | 431 | 430 | 120 mm² |  | 41 | 45 | 49 | 19 | 120 mm² |  | 25 | 36 | 29 | 19 | [32 empty] | Total Load R: 66; Total Load Y: 81; Total Load B: 78; Total Load N: 38 | 81 | 66 | 30.0935 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN4 | 23.089022, 56.812586 | 836 | Pole (PMT) | 4 | 100 | 10/06/2026, 18:28 | 1 | 248 | 250 | 250 | 433 | 437 | 433 | 120 mm² |  | 25 | 31 | 28 | 11 | [38 empty] | Total Load R: 25; Total Load Y: 31; Total Load B: 28; Total Load N: 11 | 31 | 25 | 23.2493 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.089007, 56.812575 | 835 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:27 | 1 | 247 | 248 | 249 | 431 | 433 | 432 | 120 mm² |  | 21 | 28 | 30 | 22 | [38 empty] | Total Load R: 21; Total Load Y: 28; Total Load B: 30; Total Load N: 22 | 30 | 21 | 22.3954 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.089015, 56.812581 | 829 | Pole (PMT) | 2 | 100 | 10/06/2026, 18:26 | 1 | 237 | 236 | 238 | 412 | 414 | 413 | 120 mm² |  | 20 | 22 | 21 | 21 | 120 mm² |  | 41 | 49 | 53 | 23 | [32 empty] | Total Load R: 61; Total Load Y: 71; Total Load B: 74; Total Load N: 44 | 74 | 61 | 52.8068 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN4 | 23.089, 56.812569 | 828 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:24 | 1 | 244 | 245 | 247 | 426 | 428 | 429 | 120 mm² |  | 56 | 59 | 48 | 10 | [38 empty] | Total Load R: 56; Total Load Y: 59; Total Load B: 48; Total Load N: 10 | 59 | 48 | 43.5334 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN4 | 23.089022, 56.812587 | 775 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:23 | 1 | 247 | 249 | 249 | 432 | 434 | 432 | 120 mm² |  | 28 | 29 | 28 | 15 | 120 mm² |  | 10 | 9 | 7 | 8 | [32 empty] | Total Load R: 38; Total Load Y: 38; Total Load B: 35; Total Load N: 23 | 38 | 35 | 28.4333 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN4 | 23.089014, 56.81258 | 774 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:22 | 1 | 248 | 249 | 249 | 432 | 434 | 432 | 120 mm² |  | 25 | 31 | 42 | 22 | [38 empty] | Total Load R: 25; Total Load Y: 31; Total Load B: 42; Total Load N: 22 | 42 | 25 | 31.4263 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.089027, 56.812591 | 773 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:19 | 1 | 241 | 243 | 244 | 421 | 424 | 423 | 120 mm² |  | 30 | 20 | 21 | 18 | 120 mm² |  | 35 | 30 | 29 | 19 | [32 empty] | Total Load R: 65; Total Load Y: 50; Total Load B: 50; Total Load N: 37 | 65 | 50 | 47.3976 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.090311, 56.812713 | 4520 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:14 | 1 | 236 | 238 | 239 | 413 | 415 | 414 | 120 mm² |  | 10 | 12 | 14 | 12 | [38 empty] | Total Load R: 10; Total Load Y: 12; Total Load B: 14; Total Load N: 12 | 14 | 10 | 10.0147 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN4 | 23.097051, 56.803499 | 772 | Pole (PMT) | 3 | 100 | 10/06/2026, 18:13 | 1 | 254 | 256 | 257 | 444 | 448 | 444 | 120 mm² |  | 8 | 5 | 10 | 9 | [38 empty] | Total Load R: 8; Total Load Y: 5; Total Load B: 10; Total Load N: 9 | 10 | 5 | 7.6903 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.087175, 56.923765 | 802 | Pole (PMT) | 3 | 315 | 08/06/2026, 15:55 | 1 | 244 | 245 | 244 | 426 | 424 | 425 | 120 mm² |  | 100 | 46 | 80 | 46 | 120 mm² |  | 84 | 95 | 123 | 32 | [32 empty] | Total Load R: 184; Total Load Y: 141; Total Load B: 203; Total Load N: 78 | 203 | 141 | 47.5506 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.086166, 56.918683 | 801 | Pole (PMT) | 3 | 100 | 08/06/2026, 15:52 | 1 | 244 | 243 | 244 | 426 | 426 | 421 | 120 mm² |  | 43 | 84 | 45 | 38 | [38 empty] | Total Load R: 43; Total Load Y: 84; Total Load B: 45; Total Load N: 38 | 84 | 43 | 61.9797 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.087806, 56.911636 | 1825 | Pole (PMT) | 5 | 100 | 08/06/2026, 15:47 | 1 | 257 | 257 | 258 | 447 | 449 | 447 | 120 mm² |  | 19 | 18 | 18 | 6 | 120 mm² |  | 12 | 11 | 5 | 8 | [32 empty] | Total Load R: 31; Total Load Y: 29; Total Load B: 23; Total Load N: 14 | 31 | 23 | 24.001 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.084868, 56.910586 | 1642 | Pole (PMT) | 3 | 315 | 08/06/2026, 15:43 | 1 | 244 | 243 | 246 | 424 | 428 | 425 | 120 mm² |  | 57 | 83 | 40 | 25 | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 57; Total Load Y: 83; Total Load B: 40; Total Load N: 25 | 83 | 40 | 19.3506 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.079794, 56.914415 | 2270 | Pole (PMT) | 3 | 315 | 08/06/2026, 15:39 | 1 | 246 | 247 | 246 | 430 | 429 | 428 | 185 mm² |  | 12 | 13 | 14 | 11 | [38 empty] | Total Load R: 12; Total Load Y: 13; Total Load B: 14; Total Load N: 11 | 14 | 12 | 3.3101 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN3 | 23.079703, 56.910783 | 800 | Pole (PMT) | 5 | 200 | 08/06/2026, 15:35 | 1 | 256 | 257 | 257 | 446 | 447 | 445 | 120 mm² |  | 25 | 36 | 33 | 34 | 185 mm² |  | 79 | 64 | 53 | 22 | [32 empty] | Total Load R: 104; Total Load Y: 100; Total Load B: 86; Total Load N: 56 | 104 | 86 | 40.1697 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN3 | 23.07803, 56.90937 | 1893 | Pole (PMT) | 3 | 315 | 08/06/2026, 15:32 | 1 | 246 | 245 | 244 | 429 | 427 | 424 | 185 mm² |  | 24 | 54 | 57 | 30 | 185 mm² |  | 18 | 20 | 24 | 11 | [32 empty] | Total Load R: 42; Total Load Y: 74; Total Load B: 81; Total Load N: 41 | 81 | 42 | 19.107 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.081436, 56.905258 | 799 | Pole (PMT) | 3 | 100 | 08/06/2026, 15:27 | 1 | 246 | 246 | 245 | 428 | 427 | 427 | 120 mm² |  | 14 | 13 | 9 | 7 | 120 mm² |  | 40 | 39 | 43 | 10 | [32 empty] | Total Load R: 54; Total Load Y: 52; Total Load B: 52; Total Load N: 17 | 54 | 52 | 40.0312 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN3 | 23.080532, 56.901341 | 798 | Pole (PMT) | 4 | 100 | 08/06/2026, 15:23 | 1 | 258 | 259 | 260 | 450 | 451 | 451 | 185 mm² |  | 23 | 19 | 18 | 22 | [38 empty] | Total Load R: 23; Total Load Y: 19; Total Load B: 18; Total Load N: 22 | 23 | 18 | 17.9267 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.082063, 56.899095 | 797 | Pole (PMT) | 3 | 100 | 08/06/2026, 15:20 | 1 | 244 | 244 | 243 | 423 | 421 | 422 | 120 mm² |  | 9 | 0 | 0 | 8 | 120 mm² |  | 78 | 83 | 56 | 19 | [32 empty] | Total Load R: 87; Total Load Y: 83; Total Load B: 56; Total Load N: 27 | 87 | 56 | 63.7412 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.086128, 56.903438 | 1643 | Pole (PMT) | 4 | 100 | 08/06/2026, 15:15 | 1 | 256 | 258 | 255 | 445 | 443 | 444 | 120 mm² |  | 88 | 81 | 80 | 16 | 120 mm² |  | 13 | 14 | 17 | 15 | [32 empty] | Total Load R: 101; Total Load Y: 95; Total Load B: 97; Total Load N: 31 | 101 | 95 | 77.847 | Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN3 | 23.089444, 56.898334 | 2307 | Pole (PMT) | 3 | 315 | 08/06/2026, 15:10 | 1 | 246 | 246 | 245 | 428 | 429 | 426 | 185 mm² |  | 10 | 9 | 9 | 3 | [38 empty] | Total Load R: 10; Total Load Y: 9; Total Load B: 9; Total Load N: 3 | 10 | 9 | 2.3534 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN3 | 23.089965, 56.893503 | 796 | Pole (PMT) | 3 | 315 | 08/06/2026, 15:06 | 1 | 245 | 245 | 245 | 428 | 427 | 424 | 120 mm² |  | 29 | 94 | 16 | 74 | 185 mm² |  | 66 | 47 | 45 | 19 | [32 empty] | Total Load R: 95; Total Load Y: 141; Total Load B: 61; Total Load N: 93 | 141 | 61 | 33.1828 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.095484, 56.896547 | 2016 | Pole (PMT) | 3 | 100 | 08/06/2026, 15:02 | 1 | 246 | 245 | 244 | 428 | 427 | 424 | 185 mm² |  | 22 | 35 | 39 | 14 | [38 empty] | Total Load R: 22; Total Load Y: 35; Total Load B: 39; Total Load N: 14 | 39 | 22 | 28.9114 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.095319, 56.898195 | 1450 | Pole (PMT) | 3 | 100 | 08/06/2026, 14:59 | 1 | 246 | 247 | 246 | 429 | 426 | 428 | 120 mm² |  | 27 | 19 | 37 | 12 | [38 empty] | Total Load R: 27; Total Load Y: 19; Total Load B: 37; Total Load N: 12 | 37 | 19 | 27.4928 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.093038, 56.904708 | 794 | Pole (PMT) | 3 | 315 | 08/06/2026, 14:55 | 1 | 246 | 246 | 245 | 430 | 428 | 425 | 120 mm² |  | 79 | 146 | 117 | 43 | 120 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 79; Total Load Y: 146; Total Load B: 117; Total Load N: 43 | 146 | 79 | 34.52 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.093658, 56.907694 | 795 | Ground (GMT) | 4 | 1000 | 08/06/2026, 14:50 | 1 | 254 | 253 | 252 | 442 | 440 | 439 | [12 empty] | 185 mm² |  | 49 | 63 | 87 | 31 | 185 mm² |  | 45 | 97 | 141 | 78 | [20 empty] | Total Load R: 94; Total Load Y: 160; Total Load B: 228; Total Load N: 109 | 228 | 94 | 17.4549 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.09611, 56.907255 | 2274 | Pole (PMT) | 3 | 315 | 08/06/2026, 14:46 | 1 | 247 | 247 | 247 | 429 | 430 | 428 | 185 mm² |  | 22 | 64 | 12 | 38 | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 22; Total Load Y: 64; Total Load B: 12; Total Load N: 38 | 64 | 12 | 15.0969 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 |  | 2142 | Ground (GMT) | 3 | 500 | 08/06/2026, 14:42 | 1 | 246 | 247 | 246 | 428 | 429 | 429 | [24 empty] | 185 mm² |  | 126 | 81 | 86 | 31 | 185 mm² |  | 76 | 60 | 71 | 9 | [8 empty] | Total Load R: 202; Total Load Y: 141; Total Load B: 157; Total Load N: 40 | 202 | 141 | 29.9492 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.101644, 56.899298 | 4648 | Pole (PMT) | 2 | 100 | 07/06/2026, 15:44 | 1 | 235 | 235 | 235 | 410 | 409 | 408 | 185 mm² |  | 3 | 12 | 17 | 12 | [38 empty] | Total Load R: 3; Total Load Y: 12; Total Load B: 17; Total Load N: 12 | 17 | 3 | 12.0724 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.101786, 56.893923 | 792 | Ground (GMT) | 3 | 1000 | 07/06/2026, 15:40 | 1 | 247 | 248 | 247 | 430 | 430 | 429 | [12 empty] | 185 mm² |  | 86 | 65 | 103 | 19 | 185 mm² |  | 99 | 67 | 82 | 39 | 185 mm² |  | 133 | 59 | 73 | 60 | 185 mm² |  | 116 | 141 | 106 | 15 | [8 empty] | Total Load R: 434; Total Load Y: 332; Total Load B: 364; Total Load N: 133 | 434 | 332 | 32.3235 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.105511, 56.892504 | 790 | Pole (PMT) | 3 | 315 | 07/06/2026, 15:35 | 1 | 244 | 246 | 246 | 428 | 426 | 427 | 120 mm² |  | 78 | 75 | 69 | 10 | 120 mm² |  | 66 | 73 | 47 | 22 | [32 empty] | Total Load R: 144; Total Load Y: 148; Total Load B: 116; Total Load N: 32 | 148 | 116 | 34.8302 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN3 | 23.119672, 56.889981 | 1933 | Pole (PMT) | 2 | 200 | 07/06/2026, 15:31 | 1 | 237 | 238 | 236 | 414 | 415 | 410 | 185 mm² |  | 11 | 13 | 20 | 13 | [38 empty] | Total Load R: 11; Total Load Y: 13; Total Load B: 20; Total Load N: 13 | 20 | 11 | 7.1707 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.121965, 56.887168 | 789 | Pole (PMT) | 2 | 315 | 07/06/2026, 15:26 | 1 | 237 | 239 | 237 | 414 | 415 | 412 | 120 mm² |  | 54 | 44 | 58 | 7 | 120 mm² |  | 69 | 41 | 115 | 73 | [32 empty] | Total Load R: 123; Total Load Y: 85; Total Load B: 173; Total Load N: 80 | 173 | 85 | 39.3819 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.112332, 56.878841 | 2250 | Pole (PMT) | 3 | 315 | 07/06/2026, 15:22 | 1 | 239 | 240 | 239 | 417 | 417 | 415 | 185 mm² |  | 53 | 47 | 56 | 12 | 185 mm² |  | 15 | 20 | 17 | 4 | [32 empty] | Total Load R: 68; Total Load Y: 67; Total Load B: 73; Total Load N: 16 | 73 | 67 | 16.7382 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN3 | 23.118025, 56.887168 | 2071 | Pole (PMT) | 3 | 315 | 07/06/2026, 15:18 | 1 | 242 | 241 | 241 | 421 | 420 | 420 | 185 mm² |  | 63 | 50 | 56 | 24 | [38 empty] | Total Load R: 63; Total Load Y: 50; Total Load B: 56; Total Load N: 24 | 63 | 50 | 14.5839 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.076702, 56.842093 | 784 | Pole (PMT) | 3 | 315 | 07/06/2026, 15:08 | 1 | 243 | 243 | 242 | 424 | 422 | 420 | 120 mm² |  | 20 | 27 | 51 | 26 | 120 mm² |  | 103 | 158 | 162 | 62 | [32 empty] | Total Load R: 123; Total Load Y: 185; Total Load B: 213; Total Load N: 88 | 213 | 123 | 49.6587 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.087429, 56.862724 | 787 | Pole (PMT) | 3 | 100 | 07/06/2026, 15:02 | 1 | 256 | 253 | 242 | 444 | 437 | 438 | 120 mm² |  | 49 | 113 | 111 | 60 | [38 empty] | Total Load R: 49; Total Load Y: 113; Total Load B: 111; Total Load N: 60 | 113 | 49 | 86.9005 | Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.089173, 56.855547 | 2247 | Pole (PMT) | 5 | 315 | 07/06/2026, 14:57 | 1 | 251 | 252 | 252 | 437 | 437 | 436 | 185 mm² |  | 55 | 42 | 37 | 29 | [38 empty] | Total Load R: 55; Total Load Y: 42; Total Load B: 37; Total Load N: 29 | 55 | 37 | 13.2158 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.088357, 56.852577 | 783 | Ground (GMT) | 3 | 1000 | 07/06/2026, 14:55 | 1 | 245 | 246 | 245 | 428 | 426 | 426 | [12 empty] | 185 mm² |  | 101 | 156 | 117 | 32 | 185 mm² |  | 138 | 93 | 100 | 29 | [20 empty] | Total Load R: 239; Total Load Y: 249; Total Load B: 217; Total Load N: 61 | 249 | 217 | 18.4588 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN3 | 23.090568, 56.827774 | 781 | Pole (PMT) | 3 | 100 | 07/06/2026, 14:49 | 1 | 249 | 248 | 248 | 432 | 432 | 432 | 120 mm² |  | 13 | 13 | 13 | 10 | [38 empty] | Total Load R: 13; Total Load Y: 13; Total Load B: 13; Total Load N: 10 | 13 | 13 | 9.7272 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN3 | 23.090568, 56.827774 | 780 | Pole (PMT) | 2 | 100 | 07/06/2026, 14:43 | 1 | 242 | 241 | 241 | 437 | 436 | 436 | 50 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN3 | 23.089591, 56.82732 | 2054 | Pole (PMT) | 3 | 200 | 07/06/2026, 14:38 | 1 | 251 | 250 | 251 | 438 | 436 | 436 | 185 mm² |  | 14 | 19 | 22 | 14 | [38 empty] | Total Load R: 14; Total Load Y: 19; Total Load B: 22; Total Load N: 14 | 22 | 14 | 8.345 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.088003, 56.818288 | 778 | Pole (PMT) | 5 | 315 | 07/06/2026, 14:33 | 1 | 253 | 253 | 253 | 439 | 440 | 440 | 240 mm² |  | 14 | 5 | 5 | 8 | 185 mm² |  | 3 | 3 | 4 | 3 | [32 empty] | Total Load R: 17; Total Load Y: 8; Total Load B: 9; Total Load N: 11 | 17 | 8 | 4.1036 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.088003, 56.818288 | 777 | Pole (PMT) | 3 | 100 | 07/06/2026, 14:29 | 1 | 253 | 253 | 252 | 440 | 440 | 440 | 120 mm² |  | 0 | 0 | 16 | 16 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 16; Total Load N: 16 | 16 | 0 | 12.1936 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.088003, 56.818288 | 756 | Pole (PMT) | 3 | 315 | 07/06/2026, 14:26 | 1 | 246 | 241 | 246 | 424 | 425 | 427 | 120 mm² |  | 25 | 10 | 16 | 17 | 120 mm² |  | 63 | 73 | 84 | 25 | [32 empty] | Total Load R: 88; Total Load Y: 83; Total Load B: 100; Total Load N: 42 | 100 | 83 | 23.314 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.082565, 56.81579 | 754 | Pole (PMT) | 3 | 100 | 07/06/2026, 14:20 | 1 | 237 | 242 | 244 | 416 | 419 | 408 | 120 mm² |  | 146 | 148 | 108 | 42 | [38 empty] | Total Load R: 146; Total Load Y: 148; Total Load B: 108; Total Load N: 42 | 148 | 108 | 106.6389 | Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.087502, 56.814775 | 4782 | Pole (PMT) | 3 | 100 | 07/06/2026, 14:18 | 1 | 251 | 250 | 252 | 436 | 436 | 438 | 185 mm² |  | 0 | 9 | 10 | 5 | [38 empty] | Total Load R: 0; Total Load Y: 9; Total Load B: 10; Total Load N: 5 | 10 | 0 | 7.5517 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.085163, 56.815111 | 2316 | Pole (PMT) | 3 | 100 | 07/06/2026, 14:12 | 1 | 245 | 245 | 244 | 426 | 426 | 426 | 185 mm² |  | 5 | 4 | 20 | 15 | [38 empty] | Total Load R: 5; Total Load Y: 4; Total Load B: 20; Total Load N: 15 | 20 | 4 | 14.7571 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN3 | 23.087502, 56.814775 | 755 | Pole (PMT) | 3 | 100 | 07/06/2026, 14:07 | 1 | 233 | 245 | 239 | 426 | 417 | 424 | 50 mm² |  | 15 | 15 | 15 | 10 | [38 empty] | Total Load R: 15; Total Load Y: 15; Total Load B: 15; Total Load N: 10 | 15 | 15 | 11.0678 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN3 | 23.088003, 56.818288 | 751 | Ground (GMT) | 3 | 1000 | 07/06/2026, 14:00 | 1 | 253 | 253 | 254 | 441 | 439 | 441 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 9 | 11 | 13 | 8 | 185 mm² |  | 76 | 46 | 43 | 30 | 185 mm² |  | 122 | 96 | 93 | 38 | 120 mm² |  | 12 | 52 | 25 | 31 | [14 empty] | Total Load R: 219; Total Load Y: 205; Total Load B: 174; Total Load N: 107 | 219 | 174 | 16.728 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN1 | 23.113755, 56.87817 | 788 | Pole (PMT) | 3 | 315 | 06/06/2026, 15:31 | 1 | 255 | 256 | 253 | 445 | 441 | 444 | 120 mm² |  | 50 | 53 | 104 | 50 | 120 mm² |  | 48 | 52 | 86 | 39 | [32 empty] | Total Load R: 98; Total Load Y: 105; Total Load B: 190; Total Load N: 89 | 190 | 98 | 46.4904 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN1 | 23.117548, 56.878789 | 2051 | Pole (PMT) | 3 | 315 | 06/06/2026, 15:27 | 1 | 244 | 244 | 243 | 424 | 423 | 423 | 185 mm² |  | 61 | 22 | 38 | 34 | 185 mm² |  | 32 | 36 | 60 | 30 | [32 empty] | Total Load R: 93; Total Load Y: 58; Total Load B: 98; Total Load N: 64 | 98 | 58 | 22.8477 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN1 | 23.119848, 56.875391 | 1465 | Pole (PMT) | 3 | 100 | 06/06/2026, 15:23 | 1 | 247 | 249 | 248 | 431 | 432 | 430 | 120 mm² |  | 55 | 33 | 42 | 19 | [38 empty] | Total Load R: 55; Total Load Y: 33; Total Load B: 42; Total Load N: 19 | 55 | 33 | 41.0583 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN1 |  | 1957 | Pole (PMT) | 3 | 100 | 06/06/2026, 15:19 | 1 | 251 | 251 | 250 | 438 | 435 | 435 | 120 mm² |  | 17 | 18 | 10 | 14 | [38 empty] | Total Load R: 17; Total Load Y: 18; Total Load B: 10; Total Load N: 14 | 18 | 10 | 13.6555 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN1 | 23.11697, 56.884284 | 805 | Pole (PMT) | 3 | 315 | 06/06/2026, 15:16 | 1 | 247 | 248 | 246 | 430 | 428 | 420 | 185 mm² |  | 14 | 13 | 36 | 21 | 120 mm² |  | 254 | 232 | 270 | 48 | [32 empty] | Total Load R: 268; Total Load Y: 245; Total Load B: 306; Total Load N: 69 | 306 | 245 | 72.3502 | Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN1 | 23.122018, 56.88533 | 1542 | Pole (PMT) | 3 | 100 | 06/06/2026, 15:12 | 1 | 245 | 241 | 244 | 427 | 425 | 421 | 120 mm² |  | 44 | 102 | 60 | 50 | [38 empty] | Total Load R: 44; Total Load Y: 102; Total Load B: 60; Total Load N: 50 | 102 | 44 | 75.4377 | Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN1 | 23.121512, 56.859878 | 04574 | Pole (PMT) | 3 | 100 | 06/06/2026, 15:02 | 1 | 249 | 249 | 249 | 433 | 434 | 433 | 120 mm² |  | 15 | 12 | 14 | 18 | [38 empty] | Total Load R: 15; Total Load Y: 12; Total Load B: 14; Total Load N: 18 | 15 | 12 | 11.2497 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN1 | 23.11605, 56.861743 | 1694 | Pole (PMT) | 3 | 100 | 06/06/2026, 14:55 | 1 | 249 | 249 | 249 | 433 | 432 | 434 | 120 mm² |  | 15 | 12 | 14 | 15 | [38 empty] | Total Load R: 15; Total Load Y: 12; Total Load B: 14; Total Load N: 15 | 15 | 12 | 11.2497 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN1 | 23.096636, 56.832971 | 782 | Pole (PMT) | 3 | 315 | 06/06/2026, 13:37 | 1 | 249 | 247 | 250 | 430 | 433 | 434 | 120 mm² |  | 78 | 139 | 47 | 79 | [38 empty] | Total Load R: 78; Total Load Y: 139; Total Load B: 47; Total Load N: 79 | 139 | 47 | 32.865 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN1 | 23.091163, 56.822699 | 2332 | Ground (GMT) | 3 | 1000 | 06/06/2026, 13:31 | 1 | 249 | 249 | 251 | 432 | 431 | 435 | 185 mm² |  | 147 | 70 | 62 | 42 | 185 mm² |  | 60 | 81 | 56 | 42 | 185 mm² |  | 126 | 145 | 145 | 14 | [26 empty] | Total Load R: 333; Total Load Y: 296; Total Load B: 263; Total Load N: 98 | 333 | 263 | 24.9166 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN1 | 23.088272, 56.821819 | 1650 | Ground (GMT) | 3 | 500 | 06/06/2026, 13:24 | 1 | 242 | 243 | 241 | 438 | 436 | 438 | [18 empty] | 185 mm² |  | 24 | 39 | 35 | 9 | 185 mm² |  | 15 | 12 | 14 | 18 | 185 mm² |  | 12 | 13 | 14 | 18 | [8 empty] | Total Load R: 51; Total Load Y: 64; Total Load B: 63; Total Load N: 45 | 64 | 51 | 9.7106 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN1 | 23.091117, 56.81463 | 2081 | Pole (PMT) | 4 | 200 | 06/06/2026, 13:18 | 1 | 252 | 252 | 253 | 436 | 440 | 439 | 120 mm² |  | 13 | 13 | 15 | 12 | 120 mm² |  | 12 | 12 | 15 | 18 | [32 empty] | Total Load R: 25; Total Load Y: 25; Total Load B: 30; Total Load N: 30 | 30 | 25 | 11.3276 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.097673, 56.802416 | 2082 | Pole (PMT) |  | 200 | 03/06/2026, 16:03 | 1 | 260 | 259 | 259 | 453 | 452 | 450 | 120 mm² |  | 15 | 20 | 71 | 15 | 120 mm² |  | 12 | 11 | 14 | 13 | [32 empty] | Total Load R: 27; Total Load Y: 31; Total Load B: 85; Total Load N: 28 | 85 | 27 | 33.3463 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.108376, 56.771744 | 1869 | Pole (PMT) |  | 100 | 03/06/2026, 15:46 | 1 | 236 | 236 | 235 | 410 | 410 | 410 | 120 mm² |  | 10 | 5 | 12 | 10 | [38 empty] | Total Load R: 10; Total Load Y: 5; Total Load B: 12; Total Load N: 10 | 12 | 5 | 8.5217 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.114949, 56.772912 | 4739 | Pole (PMT) |  | 100 | 03/06/2026, 15:40 | 1 | 248 | 247 | 249 | 432 | 432 | 433 | 185 mm² |  | 15 | 16 | 10 | 12 | [38 empty] | Total Load R: 15; Total Load Y: 16; Total Load B: 10; Total Load N: 12 | 16 | 10 | 11.9719 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.120662, 56.77431 | 2083 | Pole (PMT) |  | 200 | 03/06/2026, 15:33 | 1 | 245 | 246 | 246 | 427 | 427 | 427 | 120 mm² |  | 15 | 16 | 15 | 10 | 120 mm² |  | 87 | 88 | 84 | 5 | 120 mm² |  | 0 | 0 | 0 | 0 | [26 empty] | Total Load R: 102; Total Load Y: 104; Total Load B: 99; Total Load N: 15 | 104 | 99 | 38.4585 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN2 | 23.126902, 56.768677 | 675 | Pole (PMT) |  | 100 | 03/06/2026, 15:27 | 1 | 257 | 259 | 258 | 448 | 446 | 450 | 120 mm² |  | 24 | 16 | 26 | 12 | 120 mm² |  | 30 | 17 | 32 | 13 | [32 empty] | Total Load R: 54; Total Load Y: 33; Total Load B: 58; Total Load N: 25 | 58 | 33 | 45.0056 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.132044, 56.764228 | 693 | Pole (PMT) |  | 315 | 03/06/2026, 15:21 | 1 | 245 | 247 | 246 | 424 | 428 | 427 | 120 mm² |  | 160 | 113 | 100 | 51 | 120 mm² |  | 39 | 29 | 49 | 33 | [32 empty] | Total Load R: 199; Total Load Y: 142; Total Load B: 149; Total Load N: 84 | 199 | 142 | 46.3948 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.134675, 56.76034 | 4436 | Pole (PMT) |  | 100 | 03/06/2026, 15:13 | 1 | 248 | 249 | 248 | 432 | 431 | 433 | 120 mm² |  | 10 | 11 | 10 | 10 | [38 empty] | Total Load R: 10; Total Load Y: 11; Total Load B: 10; Total Load N: 10 | 11 | 10 | 8.2307 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN2 | 23.121935, 56.754024 | 697 | Pole (PMT) |  | 315 | 03/06/2026, 15:08 | 1 | 245 | 246 | 247 | 428 | 428 | 428 | 120 mm² |  | 138 | 143 | 138 | 30 | [38 empty] | Total Load R: 138; Total Load Y: 143; Total Load B: 138; Total Load N: 30 | 143 | 138 | 33.6535 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN2 | 23.134075, 56.752143 | 696 | Pole (PMT) |  | 100 | 03/06/2026, 14:59 | 1 | 254 | 257 | 256 | 443 | 443 | 445 | 120 mm² |  | 204 | 161 | 168 | 43 | [38 empty] | Total Load R: 204; Total Load Y: 161; Total Load B: 168; Total Load N: 43 | 204 | 161 | 156.5289 | Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.149259, 56.743558 | 4561 | Pole (PMT) |  | 100 | 03/06/2026, 14:47 | 1 | 247 | 248 | 248 | 431 | 431 | 432 | 120 mm² |  | 8 | 5 | 4 | 2 | 120 mm² |  | 8 | 9 | 5 | 7 | [32 empty] | Total Load R: 16; Total Load Y: 14; Total Load B: 9; Total Load N: 9 | 16 | 9 | 11.9442 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.141676, 56.747371 | 695 | Pole (PMT) |  | 100 | 03/06/2026, 14:40 | 1 | 244 | 246 | 246 | 426 | 426 | 428 | 120 mm² |  | 114 | 105 | 108 | 17 | [38 empty] | Total Load R: 114; Total Load Y: 105; Total Load B: 108; Total Load N: 17 | 114 | 105 | 84.1153 | Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN2 | 23.13815, 56.751157 | 1439 | Pole (PMT) |  | 100 | 03/06/2026, 14:35 | 1 | 242 | 243 | 245 | 423 | 424 | 422 | 185 mm² |  | 10 | 30 | 10 | 26 | 185 mm² |  | 27 | 30 | 23 | 13 | [32 empty] | Total Load R: 37; Total Load Y: 60; Total Load B: 33; Total Load N: 39 | 60 | 33 | 43.9594 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.134675, 56.76034 | 694 | Pole (PMT) |  | 315 | 03/06/2026, 14:29 | 1 | 252 | 255 | 255 | 439 | 439 | 444 | 120 mm² |  | 138 | 134 | 175 | 26 | 120 mm² |  | 179 | 150 | 180 | 33 | [32 empty] | Total Load R: 317; Total Load Y: 284; Total Load B: 355; Total Load N: 59 | 355 | 284 | 85.6925 | Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.13321, 56.763851 | 2035 | Pole (PMT) |  | 315 | 03/06/2026, 14:25 | 1 | 249 | 251 | 251 | 434 | 436 | 437 | 185 mm² |  | 188 | 126 | 121 | 60 |  |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 188; Total Load Y: 126; Total Load B: 121; Total Load N: 60 | 188 | 121 | 44.864 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.148345, 56.756841 | 1622 | Pole (PMT) |  | 200 | 03/06/2026, 14:19 | 1 | 246 | 246 | 247 | 426 | 429 | 430 | 185 mm² |  | 24 | 26 | 20 | 12 | 120 mm² |  | 10 | 15 | 13 | 14 | [32 empty] | Total Load R: 34; Total Load Y: 41; Total Load B: 33; Total Load N: 26 | 41 | 33 | 15.126 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.148556, 56.756677 | 698 | Pole (PMT) |  | 315 | 03/06/2026, 14:16 | 1 | 242 | 244 | 245 | 420 | 425 | 425 | 185 mm² |  | 141 | 122 | 111 | 25 | 185 mm² |  | 127 | 55 | 66 | 71 | [32 empty] | Total Load R: 268; Total Load Y: 177; Total Load B: 177; Total Load N: 96 | 268 | 177 | 61.8919 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.1567, 56.750219 | 699 | Pole (PMT) |  | 315 | 03/06/2026, 14:09 | 1 | 244 | 245 | 246 | 424 | 426 | 426 | 185 mm² |  | 16 | 5 | 5 | 14 | 120 mm² |  | 142 | 144 | 146 | 13 | [32 empty] | Total Load R: 158; Total Load Y: 149; Total Load B: 151; Total Load N: 27 | 158 | 149 | 36.836 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN2 | 23.158513, 56.752092 | 2252 | Pole (PMT) |  | 100 | 03/06/2026, 14:04 | 1 | 248 | 249 | 249 | 420 | 432 | 432 | 70 mm² |  | 5 | 10 | 5 | 11 | [38 empty] | Total Load R: 5; Total Load Y: 10; Total Load B: 5; Total Load N: 11 | 10 | 5 | 7.2746 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.108806, 56.785502 | 4717 | Pole (PMT) |  | 100 |  | 1 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN2 | 23.10512, 56.788209 | 632 | Pole (PMT) |  | 100 | 02/06/2026, 13:43 | 1 | 249 | 248 | 250 | 431 | 434 | 432 | 120 mm² |  | 20 | 55 | 18 | 31 | [38 empty] | Total Load R: 20; Total Load Y: 55; Total Load B: 18; Total Load N: 31 | 55 | 18 | 41.0583 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.095816, 56.797913 | 1850 | Pole (PMT) |  | 315 | 02/06/2026, 13:35 | 1 | 251 | 251 | 251 | 433 | 434 | 434 | 185 mm² |  | 30 | 43 | 57 | 26 | 185 mm² |  | 6 | 8 | 1 | 9 | [32 empty] | Total Load R: 36; Total Load Y: 51; Total Load B: 58; Total Load N: 35 | 58 | 36 | 13.8091 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.093792, 56.803433 | 2357 | Pole (PMT) |  | 315 | 02/06/2026, 13:30 | 1 | 251 | 252 | 253 | 436 | 437 | 438 | 185 mm² | [5 empty] | 185 mm² |  | 20 | 18 | 24 | 4 | [32 empty] | Total Load R: 20; Total Load Y: 18; Total Load B: 24; Total Load N: 4 | 24 | 18 | 5.7537 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.152959, 56.756868 | 2036 | Pole (PMT) |  | 315 | 25/05/2026, 15:14 | 1 | 239 | 241 | 241 | 416 | 418 | 419 | 185 mm² |  | 52 | 32 | 24 | 35 | 185 mm² |  | 29 | 18 | 15 | 14 | [32 empty] | Total Load R: 81; Total Load Y: 50; Total Load B: 39; Total Load N: 49 | 81 | 39 | 18.528 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.121204, 56.820909 | 4318 | Pole (PMT) |  | 100 | 25/05/2026, 14:53 | 1 | 243 | 245 | 245 | 423 | 425 | 425 | 185 mm² |  | 13 | 9 | 5 | 13 | [38 empty] | Total Load R: 13; Total Load Y: 9; Total Load B: 5; Total Load N: 13 | 13 | 5 | 9.5245 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.133021, 56.836213 | 674 | Pole (PMT) |  | 315 | 25/05/2026, 14:46 | 1 | 246 | 245 | 245 | 426 | 425 | 424 | 240 mm² |  | 15 | 18 | 17 | 19 | 120 mm² |  | 57 | 52 | 45 | 40 | [32 empty] | Total Load R: 72; Total Load Y: 70; Total Load B: 62; Total Load N: 59 | 72 | 62 | 16.8652 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN2 | 23.13871, 56.824225 | 1541 | Pole (PMT) |  | 100 |  | 1 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN2 | 23.126821, 56.816566 | 1471 | Pole (PMT) |  | 100 | 25/05/2026, 14:21 | 1 | 249 | 251 | 250 | 431 | 434 | 435 | 120 mm² |  | 23 | 20 | 15 | 22 | [38 empty] | Total Load R: 23; Total Load Y: 20; Total Load B: 15; Total Load N: 22 | 23 | 15 | 17.1698 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.129722, 56.809573 | 673 | Pole (PMT) |  | 100 | 25/05/2026, 14:11 | 1 | 243 | 241 | 243 | 420 | 420 | 421 | 120 mm² |  | 44 | 54 | 42 | 50 | [38 empty] | Total Load R: 44; Total Load Y: 54; Total Load B: 42; Total Load N: 50 | 54 | 42 | 39.2829 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.12686, 56.803771 | 635 | Pole (PMT) |  | 100 | 25/05/2026, 14:05 | 1 | 242 | 243 | 244 | 421 | 423 | 423 | 70 mm² |  | 15 | 18 | 19 | 25 | [38 empty] | Total Load R: 15; Total Load Y: 18; Total Load B: 19; Total Load N: 25 | 19 | 15 | 13.8547 | OK - No Upgrade | OK - Balanced
Wadi Alain | KUBARAH | K_LN2 | 23.126317, 56.797423 | 634 | Pole (PMT) |  | 200 | 25/05/2026, 13:59 | 1 | 239 | 240 | 242 | 415 | 417 | 418 | 120 mm² |  | 29 | 39 | 15 | 25 | 120 mm² |  | 67 | 41 | 60 | 15 | [32 empty] | Total Load R: 96; Total Load Y: 80; Total Load B: 75; Total Load N: 40 | 96 | 75 | 34.5025 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.121661, 56.78977 | 633 | Pole (PMT) |  | 200 | 25/05/2026, 13:54 | 1 | 241 | 242 | 243 | 419 | 421 | 422 | 120 mm² |  | 15 | 15 | 10 | 5 | [38 empty] | Total Load R: 15; Total Load Y: 15; Total Load B: 10; Total Load N: 5 | 15 | 10 | 5.443 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.117895, 56.783536 | 4364 | Pole (PMT) |  | 100 | 25/05/2026, 13:49 | 1 | 232 | 232 | 234 | 402 | 406 | 405 | 185 mm² |  | 29 | 20 | 20 | 9 | [38 empty] | Total Load R: 29; Total Load Y: 20; Total Load B: 20; Total Load N: 9 | 29 | 20 | 20.1922 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.107682, 56.806882 | 2333 | Pole (PMT) |  | 100 | 25/05/2026, 13:42 | 1 | 242 | 243 | 244 | 420 | 422 | 421 | 185 mm² |  | 19 | 18 | 25 | 28 | [38 empty] | Total Load R: 19; Total Load Y: 18; Total Load B: 25; Total Load N: 28 | 25 | 18 | 18.1865 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.111024, 56.803992 | 661 | Pole (PMT) |  | 315 | 25/05/2026, 13:38 | 1 | 243 | 241 | 243 | 420 | 420 | 420 | 120 mm² |  | 25 | 73 | 82 | 76 | 185 mm² |  | 12 | 18 | 24 | 35 | [32 empty] | Total Load R: 37; Total Load Y: 91; Total Load B: 106; Total Load N: 111 | 106 | 37 | 24.4797 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.108882, 56.801018 | 1723 | Pole (PMT) |  | 100 | 25/05/2026, 13:32 | 1 | 242 | 243 | 245 | 418 | 423 | 423 | 120 mm² |  | 30 | 5 | 12 | 21 | [38 empty] | Total Load R: 30; Total Load Y: 5; Total Load B: 12; Total Load N: 21 | 30 | 5 | 21.7199 | OK - No Upgrade | Need to Balance
Wadi Alain | KUBARAH | K_LN2 | 23.102432, 56.800165 | 4576 | Pole (PMT) |  | 100 | 25/05/2026, 13:27 | 1 | 244 | 244 | 246 | 4223 | 426 | 425 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced

## AL-AKHDAR
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Ibri | AL-AKHDAR | K_LN4 | 23.24558, 56.421344 | 0 | Pole (PMT) |  | 315 | 10/06/2026, 15:05 | 1 | 241 | 241 | 242 | 415 | 418 | 417 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN4 | 23.249982, 56.413378 | 493 | Pole (PMT) |  | 100 | 10/06/2026, 14:58 | 1 | 236 | 235 | 237 | 407 | 409 | 408 | 185 mm² |  | 8 | 7 | 5 | 0 | 120 mm² |  | 6 | 5 | 7 | 0 | [32 empty] | Total Load R: 14; Total Load Y: 12; Total Load B: 12; Total Load N: 0 | 14 | 12 | 9.8692 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN4 | 23.243489, 56.420375 | 492 | Pole (PMT) |  | 100 | 10/06/2026, 14:50 | 1 | 233 | 233 | 235 | 402 | 404 | 403 | 120 mm² |  | 7 | 3 | 4 | 1 | 120 mm² |  | 8 | 8 | 1 | 0 | [32 empty] | Total Load R: 15; Total Load Y: 11; Total Load B: 5; Total Load N: 1 | 15 | 5 | 10.4443 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN4 | 23.245115, 56.418975 | 4624 | Pole (PMT) |  | 100 | 10/06/2026, 14:47 | 1 | 242 | 241 | 243 | 418 | 421 | 416 | 185 mm² |  | 1 | 1 | 0 | 1 | [38 empty] | Total Load R: 1; Total Load Y: 1; Total Load B: 0; Total Load N: 1 | 1 | 0 | 0.724 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN4 | 23.242247, 56.433259 | 1425 | Ground (GMT) | 3 | 1000 | 10/06/2026, 14:37 | 1 | 246 | 244 | 244 | 421 | 422 | 419 | 185 mm² |  | 13 | 30 | 17 | 12 | 185 mm² |  | 24 | 73 | 60 | 39 | [32 empty] | Total Load R: 37; Total Load Y: 103; Total Load B: 77; Total Load N: 51 | 103 | 37 | 7.5107 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN4 | 23.241107, 56.430942 | 1778 | Ground (GMT) | 3 | 1000 | 10/06/2026, 14:29 | 1 | 244 | 244 | 243 | 419 | 423 | 421 | [18 empty] | 185 mm² |  | 36 | 77 | 128 | 40 | [20 empty] | Total Load R: 36; Total Load Y: 77; Total Load B: 128; Total Load N: 40 | 128 | 36 | 9.2893 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN4 | 23.238779, 56.431446 | 491 | Pole (PMT) |  | 315 | 10/06/2026, 14:24 | 1 | 244 | 243 | 245 | 420 | 416 | 421 | 120 mm² |  | 13 | 17 | 32 | 14 | 120 mm² |  | 31 | 18 | 83 | 45 | [32 empty] | Total Load R: 44; Total Load Y: 35; Total Load B: 115; Total Load N: 59 | 115 | 35 | 26.5581 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN4 | 23.236319, 56.43032 | 490 | Ground (GMT) | 3 | 500 | 10/06/2026, 14:17 | 1 | 243 | 242 | 245 | 418 | 423 | 419 | 185 mm² |  | 60 | 84 | 89 | 39 | 185 mm² |  | 35 | 51 | 23 | 43 | 185 mm² |  | 31 | 105 | 84 | 50 | 185 mm² |  | 7 | 9 | 20 | 9 | 185 mm² |  | 18 | 2 | 2 | 15 | [14 empty] | Total Load R: 151; Total Load Y: 251; Total Load B: 218; Total Load N: 156 | 251 | 151 | 36.3447 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN4 | 23.245231, 56.420937 | 1858 | Ground (GMT) | 3 | 1000 | 09/06/2026, 10:55 | 1 | 239 | 239 | 241 | 414 | 416 | 415 | [6 empty] | 240 mm² |  | 174 | 149 | 170 | 14 | 240 mm² |  | 163 | 166 | 161 | 9 | 240 mm² |  | 160 | 131 | 155 | 14 | [20 empty] | Total Load R: 497; Total Load Y: 446; Total Load B: 486; Total Load N: 37 | 497 | 446 | 35.6383 | OK - No Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN4 | 23.245159, 56.42079 | 1859 | Ground (GMT) | 3 | 1000 | 09/06/2026, 10:52 | 1 | 240 | 239 | 241 | 412 | 417 | 417 | [6 empty] | 240 mm² |  | 170 | 170 | 169 | 4 | 240 mm² |  | 133 | 133 | 130 | 9 | 240 mm² |  | 123 | 126 | 125 | 12 | [20 empty] | Total Load R: 426; Total Load Y: 429; Total Load B: 424; Total Load N: 25 | 429 | 424 | 30.6137 | OK - No Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN3 | 23.176912, 56.417313 | 1313 | Pole (PMT) | 3 | 315 | 09/06/2026, 10:25 | 1 | 246 | 248 | 248 | 426 | 427 | 428 | 185 mm² |  | 6 | 6 | 14 | 13 | [38 empty] | Total Load R: 6; Total Load Y: 6; Total Load B: 14; Total Load N: 13 | 14 | 6 | 3.2793 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.197626, 56.417903 | 1325 | Pole (PMT) | 3 | 100 | 09/06/2026, 10:19 | 1 | 245 | 244 | 247 | 422 | 421 | 423 | 120 mm² |  | 8 | 0 | 1 | 7 | [38 empty] | Total Load R: 8; Total Load Y: 0; Total Load B: 1; Total Load N: 7 | 8 | 0 | 5.8474 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.219313, 56.44751 | 293 | Ground (GMT) | 3 | 1000 | 09/06/2026, 10:21 | 1 | 241 | 243 | 240 | 419 | 414 | 417 | 240 mm² |  | 29 | 21 | 36 | 43 | 240 mm² |  | 61 | 124 | 168 | 3 | 240 mm² |  | 37 | 205 | 212 | 14 | [26 empty] | Total Load R: 127; Total Load Y: 350; Total Load B: 416; Total Load N: 60 | 416 | 127 | 30.1903 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.221337, 56.447309 | 40 | Ground (GMT) | 3 | 500 | 09/06/2026, 10:15 | 1 | 256 | 255 | 257 | 441 | 439 | 441 | 240 mm² |  | 6 | 11 | 29 | 10 | 240 mm² |  | 15 | 20 | 49 | 21 | [32 empty] | Total Load R: 21; Total Load Y: 31; Total Load B: 78; Total Load N: 31 | 78 | 21 | 11.9158 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.188727, 56.375465 | 1404 | Pole (PMT) | 3 | 100 | 09/06/2026, 10:06 | 1 | 245 | 246 | 247 | 423 | 426 | 426 | 50 mm² |  | 0 | 0 | 1 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 1; Total Load N: 0 | 1 | 0 | 0.73266 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.188727, 56.375465 | 1324 | Pole (PMT) | 3 | 100 | 09/06/2026, 09:59 | 1 | 236 | 234 | 234 | 408 | 407 | 403 | 120 mm² |  | 143 | 139 | 140 | 1 | [38 empty] | Total Load R: 143; Total Load Y: 139; Total Load B: 140; Total Load N: 1 | 143 | 139 | 101.0548 | Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN6 | 23.22186, 56.455611 | 35 | Ground (GMT) | 3 | 1000 | 09/06/2026, 09:59 | 1 | 243 | 243 | 246 | 414 | 425 | 422 | 240 mm² |  | 61 | 115 | 31 | 37 | [38 empty] | Total Load R: 61; Total Load Y: 115; Total Load B: 31; Total Load N: 37 | 115 | 31 | 8.2463 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.22186, 56.455611 | 34 | Ground (GMT) | 3 | 1000 | 09/06/2026, 10:01 | 1 | 243 | 243 | 246 | 414 | 425 | 422 | 240 mm² |  | 70 | 39 | 29 | 16 | [38 empty] | Total Load R: 70; Total Load Y: 39; Total Load B: 29; Total Load N: 16 | 70 | 29 | 5.0195 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.187725, 56.381981 | 1323 | Pole (PMT) | 3 | 100 | 09/06/2026, 09:55 | 1 | 248 | 245 | 245 | 427 | 427 | 425 | 120 mm² |  | 0 | 1 | 0 | 1 | [38 empty] | Total Load R: 0; Total Load Y: 1; Total Load B: 0; Total Load N: 1 | 1 | 0 | 0.73959 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.221438, 56.453842 | 33 | Ground (GMT) | 3 | 1000 | 09/06/2026, 09:53 | 1 | 244 | 244 | 247 | 421 | 425 | 424 | [12 empty] | 240 mm² |  | 29 | 9 | 26 | 14 | [6 empty] | 240 mm² |  | 0 | 11 | 18 | 19 | 185 mm² |  | 0 | 0 | 0 | 0 | [6 empty] | 50 mm² |  | 8 | 18 | 19 | 7 | 37 | 38 | 63 | 40 | 63 | 37 | 4.5939 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.189956, 56.392636 | 4509 | Pole (PMT) | 3 | 100 | 09/06/2026, 09:49 | 1 | 246 | 246 | 248 | 425 | 428 | 427 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN3 | 23.196535, 56.418734 | 1322 | Pole (PMT) | 3 | 100 | 09/06/2026, 09:43 | 1 | 249 | 246 | 245 | 431 | 428 | 425 | 120 mm² |  | 0 | 0 | 17 | 16 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 17; Total Load N: 16 | 17 | 0 | 12.6907 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.19728, 56.419346 | 1321 | Pole (PMT) | 3 | 100 | 09/06/2026, 09:38 | 1 | 240 | 240 | 241 | 415 | 418 | 417 | 120 mm² |  | 91 | 97 | 102 | 14 | [38 empty] | Total Load R: 91; Total Load Y: 97; Total Load B: 102; Total Load N: 14 | 102 | 91 | 73.3177 | Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN6 | 23.220943, 56.454812 | 32 | Ground (GMT) | 3 | 1000 | 09/06/2026, 09:40 | 1 | 243 | 243 | 245 | 418 | 423 | 414 | 240 mm² |  | 55 | 32 | 38 | 21 | 240 mm² |  | 96 | 87 | 77 | 20 | 240 mm² |  | 65 | 30 | 51 | 44 | [18 empty] | 120 mm² |  | 25 | 33 | 47 | 1 | 120 mm² |  | 14 | 30 | 1 | 19 | 255 | 212 | 214 | 105 | 255 | 212 | 18.4619 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.219832, 56.454491 | 31 | Ground (GMT) | 3 | 1000 | 09/06/2026, 09:31 | 1 | 243 | 242 | 244 | 418 | 422 | 422 | 120 mm² |  | 3 | 0 | 0 | 0 | 240 mm² |  | 28 | 56 | 62 | 16 | 240 mm² |  | 12 | 21 | 43 | 16 | 240 mm² |  | 8 | 9 | 20 | 28 | [20 empty] | Total Load R: 51; Total Load Y: 86; Total Load B: 125; Total Load N: 60 | 125 | 51 | 9.05 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.219052, 56.456708 | 36 | Ground (GMT) | 3 | 1000 | 09/06/2026, 09:22 | 1 | 237 | 237 | 239 | 409 | 411 | 413 | [12 empty] | 240 mm² |  | 32 | 33 | 19 | 18 | 240 mm² |  | 58 | 172 | 175 | 9 | 240 mm² |  | 156 | 58 | 108 | 12 | 120 mm² |  | 31 | 64 | 66 | 12 | 240 mm² |  | 85 | 203 | 220 | 13 | 240 mm² |  | 116 | 115 | 234 | 9 | 478 | 645 | 822 | 73 | 822 | 478 | 58.2312 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.218253, 56.462367 | 2144 | Ground (GMT) | 3 | 1000 | 09/06/2026, 09:14 | 1 | 243 | 243 | 246 | 418 | 422 | 422 | [24 empty] | 240 mm² |  | 51 | 55 | 54 | 18 | 240 mm² |  | 8 | 39 | 41 | 10 | 240 mm² |  | 71 | 46 | 51 | 23 | 240 mm² |  | 53 | 22 | 50 | 11 | 183 | 162 | 196 | 62 | 196 | 162 | 14.1903 | OK - No Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN6 | 23.218753, 56.458322 | 1490 | Ground (GMT) | 3 | 1000 | 09/06/2026, 09:05 | 1 | 246 | 244 | 244 | 425 | 424 | 420 | [12 empty] | 240 mm² |  | 25 | 38 | 25 | 8 | 240 mm² |  | 36 | 36 | 22 | 23 | [6 empty] | 120 mm² |  | 12 | 2 | 25 | 20 | [8 empty] | Total Load R: 73; Total Load Y: 76; Total Load B: 72; Total Load N: 51 | 76 | 72 | 5.5945 | OK - No Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN6 | 23.218753, 56.458322 | 1417 | Ground (GMT) | 3 | 1000 | 09/06/2026, 08:56 | 1 | 245 | 242 | 242 | 422 | 422 | 419 | 240 mm² |  | 186 | 195 | 211 | 64 | [38 empty] | Total Load R: 186; Total Load Y: 195; Total Load B: 211; Total Load N: 64 | 211 | 186 | 15.4225 | OK - No Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN6 | 23.218833, 56.448537 | 39 | Pole (PMT) |  | 315 | 08/06/2026, 15:16 | 1 | 242 | 239 | 242 | 415 | 420 | 417 | 120 mm² |  | 34 | 49 | 60 | 24 | 120 mm² |  | 93 | 105 | 17 | 33 | [32 empty] | Total Load R: 127; Total Load Y: 154; Total Load B: 77; Total Load N: 57 | 154 | 77 | 35.1414 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.222541, 56.444373 | 41 | Ground (GMT) | 3 | 1000 | 08/06/2026, 15:05 | 1 | 245 | 243 | 242 | 425 | 421 | 417 | [12 empty] | 185 mm² |  | 23 | 30 | 53 | 26 | 185 mm² |  | 15 | 85 | 32 | 48 | 185 mm² |  | 28 | 21 | 36 | 17 | [14 empty] | Total Load R: 66; Total Load Y: 136; Total Load B: 121; Total Load N: 91 | 136 | 66 | 10.0113 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.21866, 56.439201 | 1797 | Pole (PMT) |  | 315 | 08/06/2026, 14:59 | 1 | 244 | 242 | 242 | 421 | 425 | 423 | 185 mm² |  | 11 | 1 | 31 | 23 | 185 mm² |  | 10 | 6 | 21 | 10 | [32 empty] | Total Load R: 21; Total Load Y: 7; Total Load B: 52; Total Load N: 33 | 52 | 7 | 12.0375 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.223519, 56.443213 | 42 | Ground (GMT) | 3 | 500 |  | 1 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN6 | 23.225838, 56.439944 | 1427 | Pole (PMT) |  | 315 | 08/06/2026, 14:46 | 1 | 244 | 243 | 247 | 419 | 425 | 423 | 240 mm² |  | 64 | 69 | 30 | 39 | 185 mm² |  | 0 | 0 | 2 | 1 | [32 empty] | Total Load R: 64; Total Load Y: 69; Total Load B: 32; Total Load N: 40 | 69 | 32 | 15.8969 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.223025, 56.43288 | 1706 | Pole (PMT) | 3 | 315 | 08/06/2026, 14:42 | 1 | 244 | 245 | 248 | 422 | 424 | 426 | 185 mm² |  | 34 | 31 | 3 | 24 | 185 mm² |  | 11 | 0 | 0 | 9 | [32 empty] | Total Load R: 45; Total Load Y: 31; Total Load B: 3; Total Load N: 33 | 45 | 3 | 10.4418 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.227693, 56.43288 | 195 | Pole (PMT) | 2 | 100 | 08/06/2026, 14:36 | 1 | 231 | 231 | 233 | 398 | 401 | 402 | 185 mm² |  | 44 | 35 | 45 | 14 | 120 mm² |  | 0 | 3 | 0 | 2 | [32 empty] | Total Load R: 44; Total Load Y: 38; Total Load B: 45; Total Load N: 16 | 45 | 38 | 31.021 | OK - No Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN3 | 23.227649, 56.429218 | 516 | Pole (PMT) | 3 | 315 | 08/06/2026, 14:27 | 1 | 246 | 247 | 248 | 424 | 426 | 428 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 12 | 13 | 10 | 5 | [32 empty] | Total Load R: 12; Total Load Y: 13; Total Load B: 10; Total Load N: 5 | 13 | 10 | 3.0308 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.227865, 56.429107 | 517 | Ground (GMT) | 2 | 500 | 08/06/2026, 14:22 | 1 | 238 | 240 | 241 | 412 | 411 | 418 | [6 empty] | 185 mm² |  | 60 | 16 | 2 | 53 | [6 empty] | 240 mm² |  | 30 | 25 | 18 | 10 | [6 empty] | 240 mm² |  | 55 | 25 | 41 | 21 | [8 empty] | Total Load R: 145; Total Load Y: 66; Total Load B: 61; Total Load N: 84 | 145 | 61 | 20.6945 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.233505, 56.42627 | 503 | Ground (GMT) | 3 | 1000 |  | 1 | 248 | 247 | 249 | 426 | 430 | 427 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN3 | 23.233505, 56.42627 | 503 | Ground (GMT) | 3 | 1000 | 08/06/2026, 14:14 | 2 | 248 | 247 | 249 | 426 | 430 | 427 | [30 empty] | 185 mm² |  | 44 | 22 | 48 | 14 | 120 mm² |  | 28 | 22 | 24 | 14 | 120 mm² |  | 59 | 40 | 70 | 23 | 131 | 84 | 142 | 51 | 142 | 84 | 10.4775 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.223866, 56.446482 | 1824 | Ground (GMT) | 3 | 500 | 08/06/2026, 13:46 | 1 | 242 | 241 | 244 | 417 | 422 | 420 | [12 empty] | 185 mm² |  | 36 | 25 | 14 | 23 | 240 mm² |  | 141 | 90 | 147 | 1 | [6 empty] | 240 mm² |  | 26 | 13 | 16 | 11 | [8 empty] | Total Load R: 203; Total Load Y: 128; Total Load B: 177; Total Load N: 35 | 203 | 128 | 29.324 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.222882, 56.448434 | 1557 | Ground (GMT) | 3 | 1000 | 08/06/2026, 13:41 | 1 | 245 | 244 | 247 | 421 | 425 | 424 | [12 empty] | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 21 | 20 | 22 | 9 | 185 mm² |  | 34 | 32 | 60 | 27 | 185 mm² |  | 13 | 52 | 32 | 32 | [8 empty] | Total Load R: 68; Total Load Y: 104; Total Load B: 114; Total Load N: 68 | 114 | 68 | 8.3128 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.228274, 56.450231 | 4681 | Ground (GMT) | 3 | 1000 | 08/06/2026, 13:35 | 1 | 244 | 244 | 247 | 420 | 425 | 424 | 185 mm² |  | 151 | 111 | 189 | 57 | 185 mm² |  | 30 | 15 | 45 | 35 | 185 mm² |  | 26 | 31 | 12 | 11 | 185 mm² |  | 103 | 22 | 3 | 10 | 185 mm² |  | 8 | 11 | 10 | 4 | [14 empty] | Total Load R: 318; Total Load Y: 190; Total Load B: 259; Total Load N: 117 | 318 | 190 | 23.1333 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.229721, 56.442664 | 1634 | Ground (GMT) | 3 | 1000 | 07/06/2026, 15:28 | 1 | 244 | 244 | 246 | 421 | 423 | 424 | 185 mm² |  | 5 | 0 | 1 | 2 | 185 mm² |  | 17 | 8 | 42 | 7 | 185 mm² |  | 6 | 38 | 66 | 15 | 185 mm² |  | 3 | 11 | 11 | 9 | [20 empty] | Total Load R: 31; Total Load Y: 57; Total Load B: 120; Total Load N: 33 | 120 | 31 | 8.7503 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN2 | 23.231547, 56.431921 | 488 | Ground (GMT) | 3 | 1000 | 07/06/2026, 15:33 | 1 | 246 | 245 | 247 | 425 | 428 | 426 | 185 mm² |  | 10 | 6 | 10 | 3 | 185 mm² |  | 3 | 9 | 5 | 8 | 185 mm² |  | 1 | 5 | 2 | 1 | 185 mm² |  | 0 | 4 | 1 | 4 | [20 empty] | Total Load R: 14; Total Load Y: 24; Total Load B: 18; Total Load N: 16 | 24 | 14 | 1.7667 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.229394, 56.441123 | 519 | Ground (GMT) | 3 | 1000 | 07/06/2026, 15:21 | 1 | 243 | 244 | 246 | 422 | 423 | 424 | [18 empty] | 185 mm² |  | 0 | 43 | 1 | 41 | 185 mm² |  | 53 | 91 | 89 | 29 | 185 mm² |  | 0 | 0 | 0 | 0 | [8 empty] | Total Load R: 53; Total Load Y: 134; Total Load B: 90; Total Load N: 70 | 134 | 53 | 9.7944 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN1 | 23.22984, 56.425694 | 487 | Ground (GMT) | 3 | 1000 | 07/06/2026, 15:21 | 1 | 245 | 245 | 247 | 423 | 427 | 425 | 185 mm² |  | 0 | 0 | 2 | 0 | 185 mm² |  | 5 | 0 | 0 | 5 | 185 mm² |  | 10 | 2 | 5 | 1 | 185 mm² |  | 5 | 6 | 5 | 8 | 50 mm² |  | 0 | 0 | 0 | 0 | [14 empty] | Total Load R: 20; Total Load Y: 8; Total Load B: 12; Total Load N: 14 | 20 | 8 | 1.4653 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN2 | 23.230936, 56.426374 | 486 | Ground (GMT) | 3 | 1000 | 07/06/2026, 15:07 | 1 | 242 | 240 | 243 | 417 | 420 | 419 | 240 mm² |  | 0 | 0 | 7 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 7; Total Load N: 0 | 7 | 0 | 0.50559 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN2 | 23.230935, 56.426371 | 485 | Ground (GMT) | 2 | 1000 | 07/06/2026, 15:05 | 1 | 242 | 240 | 243 | 417 | 420 | 419 | 240 mm² |  | 1 | 4 | 4 | 0 | [38 empty] | Total Load R: 1; Total Load Y: 4; Total Load B: 4; Total Load N: 0 | 4 | 1 | 0.28891 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.230687, 56.435039 | 1862 | Ground (GMT) | 3 | 1000 | 07/06/2026, 15:07 | 1 | 243 | 244 | 246 | 419 | 422 | 425 | 240 mm² |  | 16 | 23 | 22 | 8 | 240 mm² |  | 22 | 37 | 3 | 18 | 240 mm² |  | 6 | 15 | 44 | 18 | 185 mm² |  | 166 | 135 | 68 | 50 | 185 mm² |  | 45 | 54 | 40 | 18 | 185 mm² |  | 0 | 0 | 0 | 0 | [8 empty] | Total Load R: 255; Total Load Y: 264; Total Load B: 177; Total Load N: 112 | 264 | 177 | 19.1593 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN2 | 23.230935, 56.426371 | 484 | Ground (GMT) | 3 | 1000 | 07/06/2026, 15:02 | 1 | 242 | 240 | 243 | 417 | 420 | 419 | 240 mm² |  | 167 | 179 | 223 | 86 | [38 empty] | Total Load R: 167; Total Load Y: 179; Total Load B: 223; Total Load N: 86 | 223 | 167 | 16.1065 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN1 | 23.231865, 56.430521 | 483 | Ground (GMT) | 3 | 1000 | 07/06/2026, 15:00 | 1 | 242 | 240 | 243 | 417 | 420 | 419 | 240 mm² |  | 261 | 257 | 208 | 99 | [38 empty] | Total Load R: 261; Total Load Y: 257; Total Load B: 208; Total Load N: 99 | 261 | 208 | 18.8511 | OK - No Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN3 | 23.238158, 56.436524 | 4379 | Pole (PMT) | 3 | 100 | 07/06/2026, 14:59 | 1 | 243 | 244 | 243 | 420 | 419 | 421 |  |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN1 | 23.231865, 56.430521 | 482 | Ground (GMT) | 3 | 1000 | 07/06/2026, 14:57 | 1 | 242 | 240 | 243 | 417 | 420 | 419 | 240 mm² |  | 435 | 432 | 321 | 56 | [38 empty] | Total Load R: 435; Total Load Y: 432; Total Load B: 321; Total Load N: 56 | 435 | 321 | 31.4185 | OK - No Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN1 | 23.232098, 56.428772 | 481 | Ground (GMT) | 2 | 1000 | 07/06/2026, 14:55 | 1 | 242 | 240 | 243 | 417 | 420 | 419 | 240 mm² |  | 327 | 304 | 260 | 127 | [38 empty] | Total Load R: 327; Total Load Y: 304; Total Load B: 260; Total Load N: 127 | 327 | 260 | 23.6181 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.236866, 56.433964 | 1326 | Ground (GMT) | 3 | 1000 | 07/06/2026, 14:54 | 1 | 246 | 243 | 244 | 424 | 425 | 422 | [18 empty] | 185 mm² |  | 87 | 63 | 81 | 22 | 185 mm² |  | 10 | 38 | 35 | 28 | 185 mm² |  | 66 | 121 | 63 | 50 | [8 empty] | Total Load R: 163; Total Load Y: 222; Total Load B: 179; Total Load N: 100 | 222 | 163 | 16.3034 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.233469, 56.432928 | 1635 | Ground (GMT) | 3 | 1000 | 07/06/2026, 14:42 | 1 | 233 | 233 | 234 | 399 | 404 | 405 | 120 mm² | [11 empty] | 185 mm² |  | 66 | 146 | 117 | 57 | 185 mm² |  | 64 | 80 | 89 | 17 | [20 empty] | Total Load R: 130; Total Load Y: 226; Total Load B: 206; Total Load N: 74 | 226 | 130 | 15.6186 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.232152, 56.431537 | 514 | Pole (PMT) | 3 | 315 | 07/06/2026, 14:31 | 1 | 242 | 245 | 246 | 421 | 422 | 425 | 120 mm² |  | 120 | 58 | 76 | 49 | [38 empty] | Total Load R: 120; Total Load Y: 58; Total Load B: 76; Total Load N: 49 | 120 | 58 | 27.7788 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN1 | 23.230766, 56.426285 | 480 | Ground (GMT) | 3 | 1000 | 07/06/2026, 14:52 | 1 | 242 | 240 | 243 | 417 | 420 | 419 | 240 mm² |  | 260 | 344 | 376 | 29 | [38 empty] | Total Load R: 260; Total Load Y: 344; Total Load B: 376; Total Load N: 29 | 376 | 260 | 27.1572 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.23293, 56.430214 | 513 | Pole (PMT) | 3 | 315 | 07/06/2026, 14:27 | 1 | 245 | 246 | 248 | 422 | 423 | 426 | 120 mm² |  | 0 | 10 | 0 | 10 | 120 mm² |  | 71 | 39 | 56 | 25 | [32 empty] | Total Load R: 71; Total Load Y: 49; Total Load B: 56; Total Load N: 35 | 71 | 49 | 16.4748 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.233723, 56.42891 | 502 | Pole (PMT) | 3 | 315 | 07/06/2026, 14:23 | 1 | 246 | 245 | 248 | 424 | 428 | 426 | 185 mm² |  | 1 | 0 | 12 | 10 | 70 mm² |  | 11 | 2 | 1 | 3 | 50 mm² |  | 1 | 0 | 0 | 1 | [26 empty] | Total Load R: 13; Total Load Y: 2; Total Load B: 13; Total Load N: 14 | 13 | 2 | 3.0308 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.238804, 56.421778 | 504 | Pole (PMT) | 3 | 200 | 07/06/2026, 14:16 | 1 | 245 | 243 | 247 | 421 | 428 | 425 | 70 mm² |  | 0 | 0 | 0 | 0 | 70 mm² |  | 15 | 28 | 24 | 16 | 185 mm² |  | 1 | 1 | 7 | 5 | [26 empty] | Total Load R: 16; Total Load Y: 29; Total Load B: 31; Total Load N: 21 | 31 | 16 | 11.3025 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN5 | 23.218129, 56.457598 | 1460 | Pole (PMT) |  | 315 | 06/06/2026, 14:52 | 1 | 243 | 242 | 244 | 418 | 422 | 421 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Ibri | AL-AKHDAR | K_LN3 | 23.230384, 56.431947 | 515 | Pole (PMT) | 3 | 315 | 08/06/2026, 14:04 | 1 | 246 | 245 | 244 | 426 | 421 | 421 | 120 mm² |  | 19 | 29 | 18 | 15 | 185 mm² |  | 130 | 45 | 62 | 69 | 185 mm² |  | 62 | 39 | 28 | 28 | [26 empty] | Total Load R: 211; Total Load Y: 113; Total Load B: 108; Total Load N: 112 | 211 | 108 | 49.4245 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN3 | 23.223651, 56.444775 | 1476 | Ground (GMT) | 3 | 500 | 08/06/2026, 13:57 | 1 | 239 | 240 | 242 | 411 | 415 | 417 | 120 mm² |  | 60 | 65 | 64 | 13 | [6 empty] | 185 mm² |  | 161 | 94 | 32 | 118 | 120 mm² |  | 53 | 89 | 74 | 33 | 120 mm² |  | 26 | 22 | 44 | 17 | 120 mm² |  | 45 | 12 | 43 | 28 | 120 mm² |  | 29 | 21 | 43 | 21 |  |  | Total Load R: 374; Total Load Y: 303; Total Load B: 300; Total Load N: 230 | 374 | 300 | 53.2481 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.22121, 56.453579 | 1421 | Ground (GMT) |  | 1000 | 28/05/2026, 21:24 | 1 | 245 | 244 | 245 | 423 | 427 | 425 | 240 mm² |  | 60 | 38 | 15 | 15 | 120 mm² |  | 70 | 50 | 53 | 28 | [12 empty] | 185 mm² |  | 123 | 118 | 146 | 33 | 185 mm² |  | 13 | 11 | 4 | 14 | 185 mm² |  | 1 | 9 | 0 | 7 |  |  | Total Load R: 267; Total Load Y: 226; Total Load B: 218; Total Load N: 97 | 267 | 218 | 19.562 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.22121, 56.453579 | 1421 | Ground (GMT) | 3 | 1000 | 08/06/2026, 14:39 | 2 | 242 | 241 | 244 | 416 | 421 | 418 | 240 mm² |  | 3 | 39 | 44 | 2 | 120 mm² |  | 64 | 97 | 103 | 45 | [12 empty] | 185 mm² |  | 146 | 98 | 182 | 61 | 120 mm² |  | 14 | 25 | 0 | 49 | 185 mm² |  | 7 | 8 | 8 | 6 |  |  | Total Load R: 234; Total Load Y: 267; Total Load B: 337; Total Load N: 163 | 337 | 234 | 24.282 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.219328, 56.460424 | 1456 | Ground (GMT) |  | 1000 | 28/05/2026, 21:12 | 1 | 247 | 245 | 243 | 426 | 423 | 423 | [12 empty] | 240 mm² |  | 60 | 38 | 67 | 19 | 185 mm² |  | 82 | 91 | 51 | 24 | 185 mm² |  | 7 | 0 | 1 | 4 | [14 empty] | Total Load R: 149; Total Load Y: 129; Total Load B: 119; Total Load N: 47 | 149 | 119 | 10.994 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.219328, 56.460424 | 1456 | Ground (GMT) | 3 | 1000 | 08/06/2026, 14:21 | 2 | 245 | 243 | 242 | 424 | 422 | 417 | [12 empty] | 240 mm² |  | 64 | 45 | 7 | 4 | 185 mm² |  | 26 | 123 | 33 | 77 | 240 mm² |  | 0 | 0 | 0 | 0 | [14 empty] | Total Load R: 90; Total Load Y: 168; Total Load B: 40; Total Load N: 81 | 168 | 40 | 12.3377 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.219888, 56.44952 | 1539 | Ground (GMT) |  | 1000 | 28/05/2026, 20:33 | 1 | 245 | 244 | 247 | 421 | 426 | 425 | 120 mm² |  | 1 | 1 | 0 | 2 | 185 mm² |  | 50 | 4 | 34 | 32 | 185 mm² |  | 61 | 43 | 41 | 20 | 185 mm² |  | 23 | 9 | 0 | 29 | 185 mm² |  | 35 | 23 | 1 | 34 | 185 mm² |  | 34 | 30 | 28 | 13 | 185 mm² |  | 22 | 9 | 2 | 15 | 185 mm² |  | 102 | 56 | 62 | 33 | 328 | 175 | 168 | 178 | 328 | 168 | 23.9175 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN6 | 23.219888, 56.44952 | 1539 | Ground (GMT) | 3 | 1000 | 08/06/2026, 15:29 | 2 | 242 | 243 | 246 | 417 | 424 | 422 | 120 mm² |  | 39 | 6 | 7 | 28 | 185 mm² |  | 151 | 60 | 45 | 83 | 185 mm² |  | 2 | 8 | 2 | 7 | 185 mm² |  | 11 | 8 | 12 | 11 | 185 mm² |  | 25 | 19 | 20 | 18 | 185 mm² |  | 37 | 11 | 50 | 43 | 185 mm² |  | 38 | 29 | 20 | 15 | 185 mm² |  | 152 | 38 | 58 | 89 | 455 | 179 | 214 | 294 | 455 | 179 | 32.8631 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN5 | 23.216374, 56.458335 | 2173 | Ground (GMT) |  | 1000 | 28/05/2026, 20:18 | 1 | 241 | 241 | 242 | 417 | 419 | 418 | [6 empty] | 240 mm² |  | 31 | 29 | 26 | 8 | 240 mm² |  | 25 | 30 | 26 | 11 | 240 mm² |  | 35 | 33 | 29 | 26 | 240 mm² |  | 266 | 246 | 170 | 7 | 240 mm² |  | 267 | 115 | 289 | 10 | [8 empty] | Total Load R: 624; Total Load Y: 453; Total Load B: 540; Total Load N: 62 | 624 | 453 | 45.0693 | OK - No Upgrade | Need to Balance
Ibri | AL-AKHDAR | K_LN5 | 23.216374, 56.458335 | 2173 | Ground (GMT) |  | 1000 | 06/06/2026, 15:04 | 2 | 239 | 239 | 240 | 413 | 415 | 413 | [6 empty] | 240 mm² |  | 39 | 43 | 42 | 7 | 240 mm² |  | 41 | 45 | 43 | 5 | 240 mm² |  | 42 | 35 | 42 | 15 |  |  | 175 | 278 | 187 | 7 | 240 mm² |  | 255 | 97 | 271 | 7 | [8 empty] | Total Load R: 552; Total Load Y: 498; Total Load B: 585; Total Load N: 41 | 585 | 498 | 41.8472 | OK - No Upgrade | OK - Balanced

## AL-DREEZ
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Araqi | AL-DREEZ | K_LN04 | 23.313887, 56.600545 | 389 | Ground (GMT) | 3 | 500 | 13/06/2026, 13:37 | 1 | 245 | 248 | 243 | 422 | 428 | 426 | [12 empty] | 185 mm² |  | 107 | 146 | 59 | 50 | 185 mm² |  | 51 | 70 | 40 | 29 | [12 empty] | 185 mm² |  | 78 | 11 | 31 | 50 | 185 mm² |  | 100 | 119 | 125 | 28 | 336 | 346 | 255 | 157 | 346 | 255 | 50.58 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN04 | 23.318176, 56.604767 | 531 | Pole (PMT) | 3 | 315 | 13/06/2026, 13:32 | 1 | 248 | 247 | 249 | 430 | 433 | 430 | 185 mm² |  | 70 | 60 | 90 | 34 | [38 empty] | Total Load R: 70; Total Load Y: 60; Total Load B: 90; Total Load N: 34 | 90 | 60 | 21.2795 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN04 | 23.320912, 56.609532 | 534 | Ground (GMT) | 3 | 500 | 13/06/2026, 13:28 | 1 | 248 | 247 | 245 | 428 | 429 | 432 | 50 mm² |  | 35 | 32 | 30 | 19 | 185 mm² |  | 92 | 80 | 101 | 47 | 185 mm² |  | 40 | 60 | 29 | 25 | [12 empty] | 70 mm² |  | 22 | 28 | 30 | 19 | [8 empty] | Total Load R: 189; Total Load Y: 200; Total Load B: 190; Total Load N: 110 | 200 | 189 | 29.6527 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN04 | 23.319723, 56.604351 | 532 | Ground (GMT) | 3 | 500 | 13/06/2026, 13:23 | 1 | 250 | 248 | 252 | 42 | 423 | 425 | [6 empty] | 185 mm² |  | 35 | 40 | 31 | 10 | [32 empty] | Total Load R: 35; Total Load Y: 40; Total Load B: 31; Total Load N: 10 | 40 | 31 | 0.58197 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN04 | 23.317757, 56.604309 | 1647 | Ground (GMT) | 3 | 1000 | 13/06/2026, 13:20 | 1 | 251 | 250 | 248 | 439 | 433 | 431 | [6 empty] | 185 mm² |  | 17 | 4 | 2 | 9 | 240 mm² |  | 17 | 22 | 20 | 17 | 120 mm² |  | 10 | 11 | 8 | 6 | 50 mm² |  | 7 | 34 | 3 | 15 | 50 mm² |  | 79 | 38 | 2 | 40 | 50 mm² |  | 11 | 0 | 0 | 8 | 50 mm² |  | 0 | 0 | 0 | 0 | 141 | 109 | 35 | 95 | 141 | 35 | 10.7212 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN04 |  | 550 | Ground (GMT) | 3 | 500 | 13/06/2026, 13:15 | 1 | 249 | 246 | 451 | 429 | 435 | 433 | 185 mm² |  | 30 | 38 | 30 | 19 | 70 mm² |  | 30 | 32 | 29 | 22 | 185 mm² |  | 55 | 47 | 42 | 18 | 185 mm² |  | 60 | 68 | 56 | 30 | 185 mm² |  | 26 | 25 | 22 | 17 | 185 mm² |  | 12 | 18 | 22 | 16 | 185 mm² |  | 9 | 32 | 34 | 22 |  |  | Total Load R: 222; Total Load Y: 260; Total Load B: 235; Total Load N: 144 | 260 | 222 | 38.6386 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN04 | 23.311866, 56.592556 | 2019 | Ground (GMT) | 3 | 1000 | 13/06/2026, 13:08 | 1 | 250 | 249 | 253 | 433 | 437 | 436 | [12 empty] | 240 mm² |  | 12 | 8 | 3 | 6 | 185 mm² |  | 20 | 17 | 16 | 14 | 185 mm² |  | 1 | 1 | 0 | 1 | 185 mm² |  | 10 | 65 | 13 | 46 | [8 empty] | Total Load R: 43; Total Load Y: 91; Total Load B: 32; Total Load N: 67 | 91 | 32 | 6.8248 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN04 | 23.311841, 56.589047 | 2214 | Ground (GMT) | 3 | 1000 | 13/06/2026, 13:03 | 1 | 250 | 249 | 252 | 433 | 438 | 436 | [18 empty] | 185 mm² |  | 0 | 0 | 13 | 11 | 185 mm² |  | 3 | 23 | 7 | 14 | 185 mm² |  | 136 | 100 | 105 | 40 | [8 empty] | Total Load R: 139; Total Load Y: 123; Total Load B: 125; Total Load N: 65 | 139 | 123 | 10.4247 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN07 | 23.301276, 56.625523 | 1436 | Pole (PMT) | 3 | 315 | 10/06/2026, 14:53 | 1 | 242 | 240 | 242 | 417 | 420 | 419 | 185 mm² |  | 92 | 81 | 92 | 21 | 185 mm² |  | 72 | 50 | 43 | 15 | [32 empty] | Total Load R: 164; Total Load Y: 131; Total Load B: 135; Total Load N: 36 | 164 | 131 | 37.6036 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN07 | 23.30066, 56.628206 | 579 | Ground (GMT) | 3 | 1000 | 10/06/2026, 14:49 | 1 | 241 | 242 | 245 | 429 | 426 | 428 | [12 empty] | 185 mm² |  | 38 | 55 | 36 | 20 | 185 mm² |  | 50 | 52 | 58 | 25 | 185 mm² |  | 205 | 170 | 180 | 41 | 185 mm² |  | 130 | 127 | 229 | 90 | [8 empty] | Total Load R: 423; Total Load Y: 404; Total Load B: 503; Total Load N: 176 | 503 | 404 | 37.3754 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN07 | 23.300208, 56.637541 | 2366 | Ground (GMT) | 3 | 1000 | 10/06/2026, 14:40 | 1 | 242 | 241 | 243 | 418 | 421 | 420 | 185 mm² |  | 40 | 35 | 38 | 29 | 185 mm² |  | 0 | 11 | 13 | 12 | 185 mm² |  | 88 | 89 | 110 | 35 | [26 empty] | Total Load R: 128; Total Load Y: 135; Total Load B: 161; Total Load N: 76 | 161 | 128 | 11.6564 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN07 | 23.30221, 56.635782 | 581 | Ground (GMT) | 3 | 1000 | 10/06/2026, 14:36 | 1 | 242 | 241 | 243 | 420 | 422 | 420 | [12 empty] | 185 mm² |  | 130 | 125 | 212 | 80 | 185 mm² |  | 60 | 97 | 75 | 32 | [20 empty] | Total Load R: 190; Total Load Y: 222; Total Load B: 287; Total Load N: 112 | 287 | 190 | 20.8781 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN07 | 23.303354, 56.628179 | 580 | Pole (PMT) | 3 | 200 | 10/06/2026, 14:54 | 1 | 240 | 242 | 241 | 419 | 416 | 419 | 120 mm² |  | 135 | 144 | 115 | 25 | 120 mm² |  | 45 | 30 | 70 | 40 | [32 empty] | Total Load R: 180; Total Load Y: 174; Total Load B: 185; Total Load N: 65 | 185 | 174 | 67.13 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN07 | 23.31093, 56.629866 | 1839 | Pole (PMT) |  | 315 | 06/06/2026, 00:38 | 1 | 241 | 242 | 243 | 416 | 424 | 420 | 185 mm² |  | 90 | 106 | 69 | 44 | 185 mm² |  | 154 | 130 | 122 | 31 | [32 empty] | Total Load R: 244; Total Load Y: 236; Total Load B: 191; Total Load N: 75 | 244 | 191 | 55.8127 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN07 | 23.31093, 56.629866 | 1839 | Pole (PMT) | 3 | 315 | 04/06/2026, 14:11 | 2 | 241 | 242 | 243 | 416 | 424 | 420 | 185 mm² |  | 168 | 145 | 60 | 97 | 185 mm² |  | 220 | 210 | 136 | 98 | [32 empty] | Total Load R: 388; Total Load Y: 355; Total Load B: 196; Total Load N: 195 | 388 | 196 | 88.7514 | Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN07 | 23.31093, 56.629866 | 1839 | Pole (PMT) |  | 315 | 05/06/2026, 13:11 | 3 | 242 | 241 | 243 | 417 | 422 | 421 | 185 mm² |  | 148 | 131 | 61 | 87 | 185 mm² |  | 215 | 117 | 139 | 97 | [32 empty] | Total Load R: 363; Total Load Y: 248; Total Load B: 200; Total Load N: 184 | 363 | 200 | 83.2325 | Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN07 | 23.311777, 56.634903 | 4795 | Ground (GMT) |  | 1000 | 03/06/2026, 14:45 | 1 | 240 | 240 | 241 | 415 | 422 | 419 | [12 empty] | 185 mm² |  | 56 | 10 | 34 | 36 | 185 mm² |  | 145 | 140 | 101 | 62 | 185 mm² |  | 45 | 50 | 12 | 10 | 185 mm² |  | 140 | 120 | 101 | 49 | 185 mm² |  | 68 | 71 | 36 | 50 |  |  | Total Load R: 454; Total Load Y: 391; Total Load B: 284; Total Load N: 207 | 454 | 284 | 32.6336 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN07 | 23.309955, 56.638415 | 443 | Pole (PMT) |  | 315 | 03/06/2026, 14:40 | 1 | 242 | 241 | 243 | 418 | 422 | 419 | 185 mm² |  | 101 | 99 | 98 | 17 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 30 | 38 | 41 | 25 | [26 empty] | Total Load R: 131; Total Load Y: 137; Total Load B: 139; Total Load N: 42 | 139 | 131 | 31.9478 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN07 | 23.308478, 56.63379 | 1446 | Pole (PMT) |  | 315 | 03/06/2026, 14:36 | 1 | 240 | 242 | 241 | 411 | 420 | 418 | 185 mm² |  | 65 | 38 | 44 | 20 | 185 mm² |  | 35 | 75 | 41 | 22 | [32 empty] | Total Load R: 100; Total Load Y: 113; Total Load B: 85; Total Load N: 42 | 113 | 85 | 25.537 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN07 | 23.307968, 56.628478 | 441 | Ground (GMT) |  | 1000 | 03/06/2026, 14:32 | 1 | 243 | 240 | 243 | 418 | 422 | 418 | 120 mm² |  | 60 | 65 | 40 | 30 | [6 empty] | 185 mm² |  | 80 | 85 | 70 | 40 | 120 mm² |  | 30 | 95 | 130 | 60 | [6 empty] | 185 mm² |  | 175 | 180 | 160 | 51 | 185 mm² |  | 30 | 45 | 60 | 20 | 185 mm² |  | 120 | 110 | 85 | 38 | 495 | 580 | 545 | 239 | 580 | 495 | 41.9918 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN07 | 23.30766, 56.623553 | 444 | Pole (PMT) |  | 315 | 06/06/2026, 00:33 | 1 | 247 | 247 | 249 | 426 | 423 | 430 | 120 mm² |  | 70 | 75 | 126 | 48 | 120 mm² |  | 96 | 72 | 40 | 54 | [32 empty] | Total Load R: 166; Total Load Y: 147; Total Load B: 166; Total Load N: 102 | 166 | 147 | 38.8837 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN07 | 23.30766, 56.623553 | 444 | Pole (PMT) | 3 | 315 | 05/06/2026, 13:02 | 2 | 246 | 245 | 248 | 424 | 429 | 428 | 120 mm² |  | 125 | 87 | 116 | 49 | 120 mm² |  | 181 | 120 | 76 | 68 | [32 empty] | Total Load R: 306; Total Load Y: 207; Total Load B: 192; Total Load N: 117 | 306 | 192 | 71.3407 | Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN04 |  | 434 | Ground (GMT) |  | 1000 | 02/06/2026, 21:57 | 1 | 249 | 247 | 250 | 430 | 434 | 431 | 185 mm² |  | 60 | 128 | 83 | 129 | 185 mm² |  | 112 | 168 | 50 | 71 |  |  | 106 | 104 | 35 | 50 | [26 empty] | Total Load R: 278; Total Load Y: 400; Total Load B: 168; Total Load N: 250 | 400 | 168 | 29.7913 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN04 |  | 433 | Ground (GMT) |  | 500 | 02/06/2026, 21:54 | 1 | 249 | 247 | 250 | 430 | 433 | 432 | 185 mm² |  | 118 | 98 | 126 | 50 | 185 mm² |  | 94 | 81 | 100 | 25 | [32 empty] | Total Load R: 212; Total Load Y: 179; Total Load B: 226; Total Load N: 75 | 226 | 179 | 33.6641 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN04 |  | 533 | Ground (GMT) |  | 500 | 02/06/2026, 21:53 | 1 | 235 | 234 | 232 | 411 | 405 | 409 | 185 mm² |  | 194 | 167 | 131 | 155 | 185 mm² |  | 155 | 189 | 121 | 68 | [32 empty] | Total Load R: 349; Total Load Y: 356; Total Load B: 252; Total Load N: 223 | 356 | 252 | 50.6853 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN05 |  | 432 | Ground (GMT) |  | 1000 | 02/06/2026, 21:52 | 1 | 248 | 248 | 251 | 431 | 436 | 434 | 185 mm² |  | 137 | 101 | 128 | 140 | 185 mm² |  | 97 | 93 | 17 | 97 |  |  | 57 | 48 | 51 | 62 |  |  | 83 | 90 | 80 | 103 | [20 empty] | Total Load R: 374; Total Load Y: 332; Total Load B: 276; Total Load N: 402 | 374 | 276 | 27.9196 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN07 | 23.312064, 56.617949 | 446 | Pole (PMT) |  | 315 | 02/06/2026, 15:09 | 1 | 243 | 241 | 243 | 420 | 415 | 423 | 240 mm² |  | 108 | 68 | 39 | 33 | 240 mm² |  | 29 | 72 | 91 | 33 | [32 empty] | Total Load R: 137; Total Load Y: 140; Total Load B: 130; Total Load N: 66 | 140 | 130 | 32.3316 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN07 | 23.309541, 56.616952 | 1319 | Ground (GMT) |  | 1000 | 02/06/2026, 15:03 | 1 | 243 | 240 | 243 | 419 | 418 | 422 | 120 mm² |  | 73 | 84 | 74 | 12 | 120 mm² |  | 130 | 74 | 123 | 50 | 120 mm² |  | 80 | 105 | 6 | 103 | 185 mm² |  | 172 | 152 | 216 | 32 | [20 empty] | Total Load R: 455; Total Load Y: 415; Total Load B: 419; Total Load N: 197 | 455 | 415 | 33.0207 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN07 | 23.30969, 56.618654 | 445 | Ground (GMT) |  | 1000 | 02/06/2026, 14:55 | 1 | 236 | 235 | 237 | 408 | 409 | 412 | [6 empty] | 185 mm² |  | 50 | 24 | 72 | 35 | 185 mm² |  | 129 | 154 | 129 | 35 | 120 mm² |  | 56 | 13 | 124 | 60 | 120 mm² |  | 143 | 84 | 86 | 62 | 120 mm² |  | 74 | 40 | 46 | 35 | 120 mm² |  | 91 | 119 | 102 | 27 | 120 mm² |  | 43 | 76 | 1 | 70 | 586 | 510 | 560 | 324 | 586 | 510 | 41.4113 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN07 | 23.312059, 56.620984 | 440 | Ground (GMT) |  | 1000 | 02/06/2026, 14:44 | 1 | 245 | 242 | 244 | 422 | 423 | 425 | [12 empty] | 185 mm² |  | 40 | 84 | 61 | 27 | 185 mm² |  | 25 | 39 | 32 | 16 | 185 mm² |  | 19 | 15 | 23 | 13 | 185 mm² |  | 69 | 73 | 165 | 89 | 185 mm² |  | 68 | 24 | 106 | 62 |  |  | Total Load R: 221; Total Load Y: 235; Total Load B: 387; Total Load N: 207 | 387 | 221 | 28.2868 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN07 |  | 439 | Ground (GMT) |  | 500 | 02/06/2026, 14:24 | 1 | 246 | 245 | 247 | 424 | 425 | 430 | 185 mm² | [7 empty] | 2 | 0 | 0 | 2 | [32 empty] | Total Load R: 2; Total Load Y: 0; Total Load B: 0; Total Load N: 2 | 2 | 0 | 0.29376 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN04 |  | 2223 | Pole (PMT) |  | 100 |  | 1 | [50 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN05 | 23.320597, 56.613253 | 1841 | Ground (GMT) |  | 1000 | 29/05/2026, 13:26 | 1 | 245 | 243 | 247 | 423 | 430 | 436 | [18 empty] | 185 mm² |  | 100 | 72 | 60 | 30 | 240 mm² |  | 41 | 30 | 22 | 15 | 240 mm² |  | 40 | 45 | 54 | 20 | 240 mm² |  | 130 | 105 | 60 | 67 | 240 mm² |  | 40 | 30 | 40 | 20 | 351 | 282 | 236 | 152 | 351 | 236 | 25.7163 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN05 | 23.318032, 56.614303 | 448 | Ground (GMT) |  | 1000 | 29/05/2026, 13:21 | 1 | 239 | 239 | 240 | 415 | 417 | 419 | 240 mm² |  | 120 | 90 | 88 | 35 | 240 mm² |  | 0 | 0 | 0 | 0 | 240 mm² |  | 40 | 76 | 70 | 10 | 240 mm² |  | 20 | 40 | 58 | 26 | 185 mm² |  | 102 | 65 | 90 | 29 | [14 empty] | Total Load R: 282; Total Load Y: 271; Total Load B: 306; Total Load N: 100 | 306 | 271 | 21.9953 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN05 | 23.319347, 56.611632 | 449 | Ground (GMT) |  | 1000 | 29/05/2026, 13:13 | 1 | 245 | 244 | 247 | 424 | 429 | 425 | [6 empty] | 185 mm² |  | 105 | 103 | 143 | 35 | 185 mm² |  | 126 | 85 | 75 | 45 | 185 mm² |  | 60 | 160 | 145 | 50 | 185 mm² |  | 43 | 15 | 17 | 28 | 185 mm² |  | 96 | 13 | 8 | 64 | [8 empty] | Total Load R: 430; Total Load Y: 376; Total Load B: 388; Total Load N: 222 | 430 | 376 | 31.5788 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN05 | 23.315716, 56.609813 | 2072 | Pole (PMT) |  | 315 | 29/05/2026, 13:07 | 1 | 244 | 244 | 244 | 422 | 429 | 426 | 185 mm² |  | 50 | 57 | 40 | 29 | 185 mm² |  | 180 | 100 | 110 | 70 | [32 empty] | Total Load R: 230; Total Load Y: 157; Total Load B: 150; Total Load N: 99 | 230 | 150 | 53.3692 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN05 |  | 429 | Ground (GMT) |  | 1000 | 29/05/2026, 13:01 | 1 | 247 | 246 | 250 | 428 | 434 | 431 | [12 empty] | 120 mm² |  | 70 | 60 | 33 | 60 | 185 mm² |  | 9 | 31 | 36 | 22 | 185 mm² |  | 7 | 15 | 90 | 78 | 185 mm² |  | 27 | 25 | 2 | 36 | 185 mm² |  | 51 | 14 | 27 | 35 |  |  | Total Load R: 164; Total Load Y: 145; Total Load B: 188; Total Load N: 231 | 188 | 145 | 13.9368 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN05 | 23.315953, 56.615532 | 428 | Ground (GMT) |  | 1000 | 29/05/2026, 12:52 | 1 | 249 | 247 | 250 | 430 | 435 | 432 | 185 mm² |  | 40 | 50 | 60 | 10 | 185 mm² |  | 110 | 40 | 52 | 48 | 185 mm² |  | 25 | 40 | 82 | 56 | 185 mm² |  | 100 | 60 | 90 | 35 | 185 mm² |  | 10 | 60 | 92 | 25 | [14 empty] | Total Load R: 285; Total Load Y: 250; Total Load B: 376; Total Load N: 174 | 376 | 250 | 28.0038 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN05 | 23.317262, 56.616382 | 1665 | Ground (GMT) |  | 1000 | 06/06/2026, 00:26 | 1 | 254 | 255 | 257 | 441 | 447 | 443 | [12 empty] | 185 mm² |  | 75 | 54 | 28 | 36 | 185 mm² |  | 191 | 123 | 152 | 51 | 185 mm² |  | 175 | 84 | 169 | 93 | [6 empty] | 185 mm² |  | 70 | 120 | 42 | 79 |  |  | Total Load R: 511; Total Load Y: 381; Total Load B: 391; Total Load N: 259 | 511 | 381 | 39.0319 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN05 | 23.317262, 56.616382 | 1665 | Ground (GMT) |  | 1000 | 05/06/2026, 13:32 | 2 | 251 | 250 | 254 | 433 | 441 | 438 | [12 empty] | 185 mm² |  | 98 | 85 | 57 | 41 | 185 mm² |  | 230 | 211 | 200 | 81 | 185 mm² |  | 162 | 184 | 153 | 36 | [6 empty] | 185 mm² |  | 89 | 90 | 22 | 77 |  |  | Total Load R: 579; Total Load Y: 570; Total Load B: 432; Total Load N: 235 | 579 | 432 | 43.4237 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN05 | 23.317231, 56.616319 | 430 | Ground (GMT) |  | 1000 | 29/05/2026, 12:43 | 1 | 248 | 246 | 250 | 428 | 434 | 430 | [12 empty] | 185 mm² |  | 105 | 155 | 80 | 69 | 185 mm² |  | 91 | 113 | 90 | 50 | 185 mm² |  | 258 | 155 | 110 | 120 | 185 mm² |  | 70 | 90 | 110 | 45 | 185 mm² |  | 50 | 40 | 105 | 66 |  |  | Total Load R: 574; Total Load Y: 553; Total Load B: 495; Total Load N: 350 | 574 | 495 | 42.5516 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN05 | 23.317231, 56.616319 | 430 | Ground (GMT) |  | 1000 | 06/06/2026, 00:22 | 2 | 245 | 244 | 248 | 421 | 432 | 428 | 185 mm² | [11 empty] | 185 mm² |  | 93 | 110 | 69 | 41 | 120 mm² |  | 53 | 101 | 93 | 38 | 185 mm² |  | 212 | 154 | 241 | 89 | 185 mm² |  | 113 | 95 | 109 | 25 | 185 mm² |  | 53 | 59 | 107 | 51 |  |  | Total Load R: 524; Total Load Y: 519; Total Load B: 619; Total Load N: 244 | 619 | 519 | 45.1371 | OK - No Upgrade | Need to Balance
Araqi | AL-DREEZ | K_LN05 |  | 2294 | Pole (PMT) |  | 315 | 29/05/2026, 12:36 | 1 | 250 | 22 | 252 | 433 | 438 | 436 | 185 mm² |  | 34 | 38 | 25 | 10 | 185 mm² |  | 10 | 15 | 0 | 8 | 185 mm² |  | 6 | 8 | 39 | 15 | [26 empty] | Total Load R: 50; Total Load Y: 61; Total Load B: 64; Total Load N: 33 | 64 | 50 | 15.2376 | OK - No Upgrade | OK - Balanced
Araqi | AL-DREEZ | K_LN05 | 23.318468, 56.616834 | 431 | Ground (GMT) |  | 1000 | 29/05/2026, 12:28 | 1 | 249 | 248 | 246 | 432 | 434 | 437 | 185 mm² |  | 63 | 58 | 25 | 36 | 185 mm² |  | 40 | 15 | 1 | 27 | 185 mm² |  | 50 | 10 | 36 | 20 | 185 mm² |  | 120 | 60 | 90 | 50 | 185 mm² |  | 70 | 170 | 160 | 85 | 185 mm² |  | 63 | 90 | 90 | 30 | 185 mm² |  | 120 | 80 | 90 | 50 | 185 mm² |  | 21 | 28 | 20 | 10 | 547 | 511 | 512 | 308 | 547 | 511 | 40.9291 | OK - No Upgrade | OK - Balanced

## BAAT
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Araqi | BAAT | K_LN02 |  | 686 | Ground (GMT) |  | 500 | 02/06/2026, 22:02 | 1 | 239 | 239 | 241 | 413 | 417 | 418 | 185 mm² |  | 154 | 135 | 145 | 44 | 185 mm² |  | 162 | 132 | 155 | 125 | [32 empty] | Total Load R: 316; Total Load Y: 267; Total Load B: 300; Total Load N: 169 | 316 | 267 | 45.2093 | OK - No Upgrade | OK - Balanced
Araqi | BAAT | K_LN01 | 23.308061, 56.586232 | 556 | Ground (GMT) |  | 500 | 02/06/2026, 22:00 | 1 | 232 | 230 | 230 | 401 | 399 | 402 | 185 mm² |  | 90 | 79 | 97 | 82 | 185 mm² |  | 117 | 160 | 130 | 122 | [32 empty] | Total Load R: 207; Total Load Y: 239; Total Load B: 227; Total Load N: 204 | 239 | 207 | 33.1996 | OK - No Upgrade | OK - Balanced
Araqi | BAAT | K_LN04 | 23.288408, 56.762008 | 1732 | Pole (PMT) |  | 100 | 01/06/2026, 13:39 | 1 | 246 | 248 | 251 | 428 | 435 | 433 | 120 mm² |  | 77 | 34 | 23 | 46 | [38 empty] | Total Load R: 77; Total Load Y: 34; Total Load B: 23; Total Load N: 46 | 77 | 23 | 57.0815 | OK - No Upgrade | Need to Balance
Araqi | BAAT | K_LN04 | 23.298268, 56.758482 | 1821 | Pole (PMT) |  | 50 | 01/06/2026, 13:14 | 1 | 252 | 242 | 254 | 442 | 439 | 437 | 120 mm² |  | 3 | 1 | 0 | 2 | [38 empty] | Total Load R: 3; Total Load Y: 1; Total Load B: 0; Total Load N: 2 | 3 | 0 | 4.5934 | OK - No Upgrade | Need to Balance
Araqi | BAAT | K_LN04 | 23.289927, 56.756212 | 639 | Pole (PMT) |  | 200 | 01/06/2026, 13:09 | 1 | 251 | 250 | 254 | 436 | 442 | 438 | 185 mm² |  | 45 | 42 | 11 | 40 | 120 mm² |  | 75 | 94 | 73 | 45 | [32 empty] | Total Load R: 120; Total Load Y: 136; Total Load B: 84; Total Load N: 85 | 136 | 84 | 51.3518 | OK - No Upgrade | Need to Balance
Araqi | BAAT | K_LN04 | 23.286648, 56.751918 | 1838 | Pole (PMT) |  | 315 | 01/06/2026, 13:04 | 1 | 254 | 252 | 254 | 438 | 442 | 440 | 185 mm² |  | 0 | 0 | 33 | 29 | 185 mm² |  | 1 | 10 | 20 | 31 | [32 empty] | Total Load R: 1; Total Load Y: 10; Total Load B: 53; Total Load N: 60 | 53 | 1 | 12.7644 | OK - No Upgrade | Need to Balance
Araqi | BAAT | K_LN40 | 23.285235, 56.747613 | 637 | Pole (PMT) |  | 315 | 01/06/2026, 12:59 | 1 | 252 | 252 | 254 | 442 | 429 | 417 | 120 mm² |  | 142 | 104 | 105 | 45 | [38 empty] | Total Load R: 142; Total Load Y: 104; Total Load B: 105; Total Load N: 45 | 142 | 104 | 34.5112 | OK - No Upgrade | Need to Balance
Araqi | BAAT | K_LN04 | 23.281738, 56.745783 | 1725 | Pole (PMT) |  | 315 | 01/06/2026, 12:52 | 1 | 251 | 252 | 252 | 437 | 435 | 438 | 185 mm² |  | 88 | 99 | 100 | 19 | 185 mm² |  | 46 | 87 | 58 | 20 | [32 empty] | Total Load R: 134; Total Load Y: 186; Total Load B: 158; Total Load N: 39 | 186 | 134 | 44.6935 | OK - No Upgrade | Need to Balance
Araqi | BAAT | K_LN04 | 23.277835, 56.740697 | 4588 | Ground (GMT) |  | 500 | 01/06/2026, 12:46 | 1 | 247 | 250 | 249 | 439 | 429 | 436 | 185 mm² |  | 80 | 122 | 81 | 85 | 185 mm² |  | 68 | 66 | 85 | 19 | [32 empty] | Total Load R: 148; Total Load Y: 188; Total Load B: 166; Total Load N: 104 | 188 | 148 | 28.5899 | OK - No Upgrade | Need to Balance
Araqi | BAAT | K_LN04 | 23.280487, 56.751232 | 4644 | Pole (PMT) |  | 100 | 31/05/2026, 13:30 | 1 | 253 | 253 | 255 | 440 | 443 | 443 | 185 mm² |  | 21 | 0 | 13 | 11 | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 21; Total Load Y: 0; Total Load B: 13; Total Load N: 11 | 21 | 0 | 16.0041 | OK - No Upgrade | Need to Balance
Araqi | BAAT | K_LN04 | 23.28303, 56.756741 | 4205 | Ground (GMT) |  | 1000 | 31/05/2026, 13:26 | 1 | 255 | 253 | 256 | 440 | 443 | 445 | [30 empty] | 185 mm² |  | 22 | 18 | 10 | 16 | 185 mm² |  | 15 | 33 | 21 | 6 | 185 mm² |  | 0 | 6 | 12 | 11 | 37 | 57 | 43 | 33 | 57 | 37 | 4.344 | OK - No Upgrade | Need to Balance
Araqi | BAAT | K_LN04 | 23.286017, 56.764945 | 4202 | Pole (PMT) |  | 315 | 31/05/2026, 13:20 | 1 | 254 | 252 | 255 | 438 | 439 | 443 | 185 mm² |  | 10 | 17 | 17 | 10 | 185 mm² |  | 0 | 3 | 0 | 3 | 185 mm² |  | 0 | 0 | 0 | 0 | [26 empty] | Total Load R: 10; Total Load Y: 20; Total Load B: 17; Total Load N: 13 | 20 | 10 | 4.8168 | OK - No Upgrade | Need to Balance
Araqi | BAAT | K_LN04 | 23.287152, 56.76873 | 2125 | Pole (PMT) |  | 315 | 31/05/2026, 13:16 | 1 | 255 | 254 | 256 | 441 | 444 | 445 | 185 mm² |  | 2 | 0 | 0 | 0 | 185 mm² |  | 2 | 6 | 10 | 7 | 185 mm² |  | 9 | 1 | 4 | 8 | [26 empty] | Total Load R: 13; Total Load Y: 7; Total Load B: 14; Total Load N: 15 | 14 | 7 | 3.3948 | OK - No Upgrade | Need to Balance
Araqi | BAAT | K_LN04 | 23.288858, 56.773667 | 2104 | Pole (PMT) |  | 315 | 31/05/2026, 13:07 | 1 | 249 | 248 | 251 | 430 | 435 | 433 | 120 mm² |  | 37 | 32 | 0 | 37 | 185 mm² |  | 11 | 0 | 0 | 13 | [32 empty] | Total Load R: 48; Total Load Y: 32; Total Load B: 0; Total Load N: 50 | 48 | 0 | 11.3491 | OK - No Upgrade | Need to Balance
Araqi | BAAT | K_LN04 | 23.290082, 56.785532 | 640 | Pole (PMT) |  | 100 | 31/05/2026, 13:00 | 1 | 255 | 251 | 253 | 441 | 441 | 438 | 185 mm² |  | 1 | 11 | 0 | 8 | 120 mm² |  | 4 | 45 | 61 | 52 | [32 empty] | Total Load R: 5; Total Load Y: 56; Total Load B: 61; Total Load N: 60 | 61 | 5 | 46.5939 | OK - No Upgrade | Need to Balance
Araqi | BAAT | K_LN04 | 23.29844, 56.78507 | 04551 | Pole (PMT) |  | 100 | 31/05/2026, 12:55 | 1 | 254 | 255 | 257 | 441 | 446 | 444 | 185 mm² |  | 3 | 1 | 0 | 3 | [38 empty] | Total Load R: 3; Total Load Y: 1; Total Load B: 0; Total Load N: 3 | 3 | 0 | 2.2915 | OK - No Upgrade | Need to Balance
Araqi | BAAT | K_LN04 | 23.300903, 56.793767 | 2180 | Pole (PMT) |  | 315 | 31/05/2026, 12:49 | 1 | 255 | 256 | 257 | 444 | 447 | 444 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 15 | 0 | 1 | 12 | [32 empty] | Total Load R: 15; Total Load Y: 0; Total Load B: 1; Total Load N: 12 | 15 | 0 | 3.6621 | OK - No Upgrade | Need to Balance

## AL TAYYEB INDUSTRIAL
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Feeder 9 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Araqi | AL TAYYEB INDUSTRIAL | K_LN04 | 23.24115, 56.551532 | 1469 | Ground (GMT) |  | 1000 | 12/06/2026, 13:04 | 1 | 250 | 248 | 249 | 433 | 439 | 431 | 185 mm² |  | 42 | 64 | 69 | 32 | 185 mm² |  | 47 | 31 | 14 | 24 | 185 mm² |  | 18 | 5 | 3 | 11 | 185 mm² |  | 42 | 28 | 69 | 35 | [26 empty] | Total Load R: 149; Total Load Y: 128; Total Load B: 155; Total Load N: 102 | 155 | 128 | 11.6247 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN04 | 23.245182, 56.549351 | 1699 | Ground (GMT) |  | 500 | 12/06/2026, 12:55 | 1 | 252 | 249 | 251 | 447 | 438 | 436 | [12 empty] | 185 mm² |  | 4 | 2 | 0 | 3 | 185 mm² |  | 26 | 20 | 17 | 11 | 185 mm² |  | 17 | 15 | 19 | 8 | 185 mm² |  | 23 | 19 | 40 | 31 | [14 empty] | Total Load R: 70; Total Load Y: 56; Total Load B: 76; Total Load N: 53 | 76 | 56 | 11.7682 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN04 | 23.24845, 56.550522 | 1561 | Ground (GMT) | 3 | 1000 | 12/06/2026, 12:47 | 1 | 253 | 253 | 251 | 442 | 438 | 436 | 185 mm² | [23 empty] | 185 mm² |  | 23 | 45 | 32 | 15 | 185 mm² |  | 50 | 19 | 3 | 42 | 185 mm² |  | 1 | 22 | 4 | 15 | 185 mm² |  | 44 | 14 | 20 | 16 |  |  | Total Load R: 118; Total Load Y: 100; Total Load B: 59; Total Load N: 88 | 118 | 59 | 9.0337 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN02 | 23.2588, 56.537056 | 257 | Ground (GMT) | 3 | 1000 | 11/06/2026, 13:18 | 1 | 241 | 246 | 245 | 421 | 424 | 429 | 185 mm² |  | 106 | 11 | 46 | 79 | 185 mm² |  | 132 | 100 | 98 | 97 | 185 mm² |  | 12 | 9 | 1 | 2 | 185 mm² |  | 183 | 127 | 119 | 42 | [26 empty] | Total Load R: 433; Total Load Y: 247; Total Load B: 264; Total Load N: 220 | 433 | 247 | 31.5741 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN02 | 23.255623, 56.537807 | 258 | Ground (GMT) | 3 | 1000 | 11/06/2026, 13:11 | 1 | 242 | 246 | 245 | 423 | 421 | 427 | [12 empty] | 185 mm² |  | 62 | 77 | 21 | 28 | 185 mm² |  | 203 | 321 | 144 | 55 | 185 mm² |  | 37 | 13 | 81 | 46 |  |  | 160 | 120 | 136 | 2 | 185 mm² |  | 108 | 90 | 105 | 31 | [8 empty] | Total Load R: 570; Total Load Y: 621; Total Load B: 487; Total Load N: 162 | 621 | 487 | 45.498 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN02 | 23.253288, 56.544424 | 1560 | Ground (GMT) | 3 | 1000 | 11/06/2026, 13:02 | 1 | 245 | 248 | 248 | 429 | 427 | 434 | [24 empty] | 185 mm² |  | 29 | 2 | 30 | 23 | 185 mm² |  | 47 | 28 | 26 | 17 | 185 mm² |  | 67 | 35 | 63 | 21 | 185 mm² |  | 28 | 31 | 13 | 17 |  |  | Total Load R: 171; Total Load Y: 96; Total Load B: 132; Total Load N: 78 | 171 | 96 | 12.7062 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN02 | 23.255393, 56.544613 | 260 | Pole (PMT) | 3 | 315 | 11/06/2026, 12:53 | 1 | 244 | 245 | 246 | 425 | 424 | 429 | 120 mm² |  | 52 | 95 | 31 | 61 | 185 mm² |  | 129 | 129 | 136 | 218 | [38 empty] | Total Load R: 181; Total Load Y: 224; Total Load B: 167; Total Load N: 279 | 224 | 167 | 52.3464 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN02 | 23.256965, 56.544108 | 256 | Ground (GMT) | 3 | 1000 | 11/06/2026, 12:46 | 1 | 245 | 247 | 247 | 427 | 428 | 429 | [30 empty] | 185 mm² |  | 254 | 134 | 101 | 90 | 185 mm² |  | 36 | 75 | 60 | 14 | 185 mm² |  | 20 | 62 | 52 | 22 |  |  | Total Load R: 310; Total Load Y: 271; Total Load B: 213; Total Load N: 126 | 310 | 213 | 22.9272 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.255211, 56.577495 | 1398 | Ground (GMT) |  | 1000 | 09/06/2026, 15:11 | 1 | 243 | 244 | 242 | 422 | 419 | 422 | [12 empty] | 185 mm² |  | 154 | 83 | 42 | 68 | 185 mm² |  | 1 | 9 | 9 | 8 | 185 mm² |  | 74 | 63 | 64 | 29 | [20 empty] | Total Load R: 229; Total Load Y: 155; Total Load B: 115; Total Load N: 105 | 229 | 115 | 16.7382 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.257398, 56.57336 | 423 | Ground (GMT) |  | 1000 | 09/06/2026, 14:58 | 1 | 243 | 244 | 242 | 423 | 420 | 422 | 185 mm² |  | 84 | 74 | 74 | 45 | 185 mm² |  | 163 | 107 | 48 | 63 | [14 empty] | 70 | 23 | 114 | 75 | 185 mm² |  | 66 | 91 | 76 | 22 | [14 empty] | Total Load R: 383; Total Load Y: 295; Total Load B: 312; Total Load N: 205 | 383 | 295 | 28.0608 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.233734, 56.602644 | 1987 | Ground (GMT) | 3 | 1000 | 09/06/2026, 14:55 | 1 | 245 | 247 | 243 | 429 | 422 | 427 | [12 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 13 | 20 | 8 | 10 | 185 mm² |  | 26 | 42 | 44 | 29 | 240 mm² |  | 17 | 28 | 26 | 10 | 185 mm² |  | 0 | 0 | 0 | 0 | [8 empty] | Total Load R: 56; Total Load Y: 90; Total Load B: 78; Total Load N: 49 | 90 | 56 | 6.6874 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.237758, 56.612392 | 1855 | Ground (GMT) | 3 | 1000 | 09/06/2026, 14:48 | 1 | 245 | 247 | 243 | 429 | 423 | 427 | [18 empty] | 240 mm² |  | 1 | 10 | 9 | 6 | 185 mm² |  | 12 | 1 | 1 | 10 | 185 mm² |  | 14 | 14 | 13 | 10 | 185 mm² |  | 10 | 8 | 4 | 4 | [8 empty] | Total Load R: 37; Total Load Y: 33; Total Load B: 27; Total Load N: 30 | 37 | 27 | 2.7493 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.23478, 56.613278 | 2138 | Ground (GMT) | 3 | 1000 | 09/06/2026, 14:44 | 1 | 245 | 247 | 244 | 429 | 428 | 425 | 185 mm² |  | 15 | 0 | 1 | 8 | 185 mm² |  | 11 | 9 | 4 | 7 | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 26; Total Load Y: 9; Total Load B: 5; Total Load N: 15 | 26 | 5 | 1.9319 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.256529, 56.570061 | 2172 | Ground (GMT) |  | 1000 | 09/06/2026, 14:47 | 1 | 244 | 245 | 242 | 426 | 419 | 424 | [24 empty] | 185 mm² |  | 88 | 102 | 69 | 32 | 185 mm² |  | 13 | 23 | 50 | 36 | 185 mm² |  | 18 | 12 | 36 | 18 | 185 mm² |  | 33 | 22 | 75 | 38 |  |  | Total Load R: 152; Total Load Y: 159; Total Load B: 230; Total Load N: 124 | 230 | 152 | 16.9706 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.232507, 56.620595 | 1931 | Ground (GMT) | 3 | 1000 | 09/06/2026, 14:41 | 1 | 243 | 245 | 241 | 425 | 424 | 426 | [18 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | [18 empty] | 185 mm² |  | 0 | 0 | 0 | 0 |  |  | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.255478, 56.567615 | 1630 | Pole (PMT) |  | 315 | 09/06/2026, 14:39 | 1 | 244 | 245 | 244 | 426 | 42 | 426 | 185 mm² |  | 98 | 8 | 3 | 40 | 185 mm² |  | 10 | 11 | 8 | 9 | [38 empty] | Total Load R: 108; Total Load Y: 19; Total Load B: 11; Total Load N: 49 | 108 | 11 | 25.2978 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.227928, 56.621712 | 1861 | Ground (GMT) | 3 | 1000 | 09/06/2026, 14:36 | 1 | 248 | 246 | 244 | 427 | 429 | 428 | [24 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | [20 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.261862, 56.568766 | 1432 | Pole (PMT) |  | 315 | 09/06/2026, 14:32 | 1 | 243 | 245 | 243 | 425 | 421 | 424 | 240 mm² |  | 13 | 0 | 0 | 12 | 185 mm² |  | 102 | 85 | 67 | 26 | [38 empty] | Total Load R: 115; Total Load Y: 85; Total Load B: 67; Total Load N: 38 | 115 | 67 | 26.8743 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.265477, 56.564552 | 422 | Pole (PMT) |  | 315 | 09/06/2026, 14:27 | 1 | 240 | 240 | 238 | 419 | 414 | 41650 | 120 mm² |  | 50 | 77 | 57 | 22 | [44 empty] | Total Load R: 50; Total Load Y: 77; Total Load B: 57; Total Load N: 22 | 77 | 50 | 17.74 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.230435, 56.616012 | 1907 | Ground (GMT) | 3 | 500 | 09/06/2026, 14:27 | 1 | 241 | 243 | 241 | 420 | 423 | 422 | [12 empty] | 185 mm² |  | 10 | 0 | 7 | 6 | 185 mm² |  | 0 | 0 | 0 | 0 | 240 mm² |  | 10 | 13 | 0 | 11 | [12 empty] | 185 mm² |  | 12 | 0 | 10 | 8 |  |  | Total Load R: 32; Total Load Y: 13; Total Load B: 17; Total Load N: 25 | 32 | 13 | 4.6558 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.270569, 56.564821 | 16890 | Pole (PMT) |  | 315 | 09/06/2026, 14:22 | 1 | 241 | 240 | 238 | 418 | 415 | 414 | 185 mm² |  | 130 | 79 | 70 | 53 | 185 mm² |  | 2 | 56 | 17 | 52 | [38 empty] | Total Load R: 132; Total Load Y: 135; Total Load B: 87; Total Load N: 105 | 135 | 87 | 31.0285 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.227142, 56.617622 | 2162 | Ground (GMT) | 3 | 1000 | 09/06/2026, 14:22 | 1 | 242 | 241 | 243 | 420 | 422 | 419 | [42 empty] | 185 mm² |  | 0 | 0 | 0 | 0 |  |  | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.22688, 56.613742 | 1854 | Ground (GMT) | 3 | 1000 | 09/06/2026, 14:17 | 1 | 241 | 243 | 240 | 424 | 425 | 423 | [24 empty] | 185 mm² |  | 10 | 0 | 0 | 5 | 185 mm² |  | 11 | 10 | 10 | 7 | [14 empty] | Total Load R: 21; Total Load Y: 10; Total Load B: 10; Total Load N: 12 | 21 | 10 | 1.5422 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.27061, 56.564839 | 1569 | Pole (PMT) |  | 315 | 09/06/2026, 14:15 | 1 | 241 | 242 | 239 | 421 | 414 | 417 | 120 mm² |  | 88 | 86 | 116 | 30 | [44 empty] | Total Load R: 88; Total Load Y: 86; Total Load B: 116; Total Load N: 30 | 116 | 86 | 26.8528 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.225217, 56.612217 | 2163 | Ground (GMT) | 3 | 1000 | 09/06/2026, 14:12 | 1 | 242 | 243 | 241 | 424 | 419 | 420 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 32 | 8 | 17 | 20 | [38 empty] | Total Load R: 32; Total Load Y: 8; Total Load B: 17; Total Load N: 20 | 32 | 8 | 2.35 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.22438, 56.608147 | 2026 | Ground (GMT) | 3 | 500 | 09/06/2026, 14:09 | 1 | 243 | 244 | 241 | 425 | 419 | 421 | [12 empty] | 185 mm² |  | 1 | 26 | 16 | 18 | 240 mm² |  | 1 | 0 | 0 | 1 | [26 empty] | Total Load R: 2; Total Load Y: 26; Total Load B: 16; Total Load N: 19 | 26 | 2 | 3.8278 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.239884, 56.599633 | 2127 | Pole (PMT) | 3 | 315 | 09/06/2026, 14:04 | 1 | 242 | 243 | 240 | 424 | 417 | 419 | 185 mm² |  | 60 | 65 | 75 | 20 | 185 mm² |  | 50 | 48 | 25 | 19 | [38 empty] | Total Load R: 110; Total Load Y: 113; Total Load B: 100; Total Load N: 39 | 113 | 100 | 26.3448 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.252218, 56.595282 | 4602 | Pole (PMT) | 3 | 100 | 09/06/2026, 13:59 | 1 | 245 | 246 | 243 | 428 | 423 | 427 | 185 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.270107, 56.554209 | 426 | Ground (GMT) |  | 1000 | 08/06/2026, 14:49 | 1 | 244 | 242 | 244 | 422 | 421 | 425 | [6 empty] | 50 mm² |  | 0 | 0 | 0 | 0 | [12 empty] | 185 mm² |  | 159 | 88 | 106 | 52 | 185 mm² |  | 1 | 37 | 19 | 23 | 185 mm² |  | 40 | 45 | 40 | 10 | 185 mm² |  | 200 | 286 | 150 | 103 |  |  | Total Load R: 400; Total Load Y: 456; Total Load B: 315; Total Load N: 188 | 456 | 315 | 33.3302 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.269521, 56.555652 | 421 | Pole (PMT) |  | 315 | 08/06/2026, 14:43 | 1 | 242 | 243 | 240 | 423 | 420 | 419 | 120 mm² |  | 64 | 126 | 98 | 38 | 120 mm² |  | 111 | 54 | 97 | 43 | [38 empty] | Total Load R: 175; Total Load Y: 180; Total Load B: 195; Total Load N: 81 | 195 | 175 | 45.355 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.267257, 56.559354 | 1445 | Pole (PMT) |  | 315 | 08/06/2026, 14:37 | 1 | 244 | 244 | 242 | 425 | 421 | 422 | 185 mm² |  | 54 | 55 | 75 | 22 | 185 mm² |  | 45 | 58 | 14 | 33 | [38 empty] | Total Load R: 99; Total Load Y: 113; Total Load B: 89; Total Load N: 55 | 113 | 89 | 26.4069 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.228491, 56.563044 | 4425 | Pole (PMT) |  | 200 | 08/06/2026, 14:43 | 1 | 243 | 245 | 246 | 422 | 425 | 428 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.228246, 56.562956 | 4521 | Pole (PMT) |  | 315 | 08/06/2026, 14:14 | 1 | 239 | 240 | 242 | 427 | 419 | 421 | 185 mm² |  | 13 | 25 | 11 | 15 | [44 empty] | Total Load R: 13; Total Load Y: 25; Total Load B: 11; Total Load N: 15 | 25 | 11 | 5.8697 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.232172, 56.566969 | 908 | Pole (PMT) |  | 315 | 08/06/2026, 14:07 | 1 | 240 | 241 | 243 | 416 | 421 | 423 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.226462, 56.571316 | 1992 | Ground (GMT) |  | 1000 | 08/06/2026, 14:01 | 1 | 240 | 242 | 243 | 418 | 419 | 422 | [12 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 0 | 0 | 21 | 15 | [26 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 21; Total Load N: 15 | 21 | 0 | 1.5204 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.273434, 56.558393 | 1689 | Pole (PMT) |  | 315 | 08/06/2026, 13:59 | 1 | 242 | 241 | 240 | 422 | 418 | 420 | 185 mm² |  | 72 | 61 | 36 | 26 | 120 mm² |  | 24 | 45 | 20 | 17 | [38 empty] | Total Load R: 96; Total Load Y: 106; Total Load B: 56; Total Load N: 43 | 106 | 56 | 24.5962 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.231995, 56.574502 | 2323 | Pole (PMT) |  | 100 | 08/06/2026, 13:57 | 1 | 126 | 242 | 115 | 369 | 132 | 358 | 50 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.229166, 56.576774 | 907 | Pole (PMT) |  | 100 | 08/06/2026, 13:50 | 1 | 243 | 244 | 240 | 424 | 418 | 420 | [6 empty] | 120 mm² |  | 0 | 2 | 14 | 14 | [38 empty] | Total Load R: 0; Total Load Y: 2; Total Load B: 14; Total Load N: 14 | 14 | 0 | 10.2815 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.274066, 56.55269 | 418 | Ground (GMT) |  | 1000 | 08/06/2026, 13:49 | 1 | 242 | 245 | 245 | 426 | 422 | 423 | 185 mm² |  | 93 | 39 | 78 | 42 | 185 mm² |  | 68 | 108 | 78 | 23 | 185 mm² |  | 92 | 88 | 73 | 32 | 185 mm² |  | 77 | 73 | 41 | 48 | 185 mm² |  | 0 | 0 | 0 | 0 | [18 empty] | 185 mm² |  | Total Load R: 330; Total Load Y: 308; Total Load B: 270; Total Load N: 145 | 330 | 270 | 24.3492 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.229099, 56.576507 | 2092 | Ground (GMT) |  | 500 | 08/06/2026, 13:44 | 1 | 243 | 244 | 246 | 423 | 423 | 427 | [36 empty] | 185 mm² |  | 2 | 0 | 1 | 2 | 185 mm² |  | 1 | 0 | 1 | 1 |  |  | Total Load R: 3; Total Load Y: 0; Total Load B: 2; Total Load N: 3 | 3 | 0 | 0.43959 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.229073, 56.576567 | 2091 | Ground (GMT) |  | 1000 | 08/06/2026, 13:42 | 1 | 243 | 244 | 246 | 424 | 423 | 429 | [6 empty] | 240 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.273522, 56.548925 | 425 | Ground (GMT) |  | 1000 | 08/06/2026, 13:41 | 1 | 242 | 244 | 244 | 422 | 425 | 422 | [12 empty] | 185 mm² |  | 151 | 111 | 129 | 30 | 185 mm² |  | 41 | 23 | 96 | 65 | 185 mm² |  | 52 | 36 | 11 | 44 | 185 mm² |  | 25 | 91 | 50 | 30 | 185 mm² |  | 136 | 106 | 143 | 48 | 185 mm² |  | 18 | 101 | 49 | 41 |  |  | Total Load R: 423; Total Load Y: 468; Total Load B: 478; Total Load N: 258 | 478 | 423 | 34.9382 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.227649, 56.584257 | 4361 | Ground (GMT) |  | 500 | 08/06/2026, 13:36 | 1 | 245 | 246 | 243 | 428 | 425 | 425 | [6 empty] | 240 mm² |  | 3 | 1 | 0 | 2 | [38 empty] | Total Load R: 3; Total Load Y: 1; Total Load B: 0; Total Load N: 2 | 3 | 0 | 0.44479 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.271761, 56.551978 | 419 | Pole (PMT) |  | 315 | 08/06/2026, 13:32 | 1 | 242 | 246 | 245 | 422 | 430 | 423 | 120 mm² |  | 130 | 57 | 70 | 61 | 120 mm² |  | 60 | 19 | 80 | 55 | [38 empty] | Total Load R: 190; Total Load Y: 76; Total Load B: 150; Total Load N: 116 | 190 | 76 | 44.0876 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.233747, 56.587091 | 906 | Pole (PMT) | 3 | 315 | 09/06/2026, 15:07 | 1 | 245 | 246 | 242 | 429 | 421 | 424 | [6 empty] | 120 mm² |  | 52 | 57 | 66 | 15 | [38 empty] | Total Load R: 52; Total Load Y: 57; Total Load B: 66; Total Load N: 15 | 66 | 52 | 15.5687 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.231028, 56.595478 | 905 | Pole (PMT) | 3 | 315 | 09/06/2026, 15:04 | 1 | 246 | 246 | 244 | 429 | 426 | 425 | 185 mm² | [5 empty] | 185 mm² |  | 4 | 24 | 4 | 17 | [38 empty] | Total Load R: 4; Total Load Y: 24; Total Load B: 4; Total Load N: 17 | 24 | 4 | 5.6613 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.268915, 56.549986 | 420 | Ground (GMT) |  | 1000 | 08/06/2026, 13:27 | 1 | 244 | 248 | 248 | 425 | 432 | 428 | [18 empty] | 185 mm² |  | 51 | 26 | 27 | 20 | 185 mm² |  | 151 | 32 | 27 | 120 | 185 mm² |  | 61 | 28 | 48 | 31 | 185 mm² |  | 186 | 115 | 101 | 83 | 185 mm² |  | 42 | 93 | 15 | 58 |  |  | Total Load R: 491; Total Load Y: 294; Total Load B: 218; Total Load N: 312 | 491 | 218 | 36.1436 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.231028, 56.595478 | 2161 | Pole (PMT) |  | 315 | 08/06/2026, 13:26 | 1 | 246 | 247 | 244 | 431 | 426 | 426 | 185 mm² |  | 22 | 17 | 26 | 10 | 185 mm² |  | 21 | 46 | 25 | 17 | [38 empty] | Total Load R: 43; Total Load Y: 63; Total Load B: 51; Total Load N: 27 | 63 | 43 | 14.9303 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.228135, 56.597035 | 2301 | Pole (PMT) |  | 200 | 08/06/2026, 13:22 | 1 | 241 | 242 | 239 | 421 | 418 | 426 | 185 mm² |  | 1 | 0 | 12 | 9 | [44 empty] | Total Load R: 1; Total Load Y: 0; Total Load B: 12; Total Load N: 9 | 12 | 0 | 4.3752 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.225832, 56.600717 | 1767 | Ground (GMT) |  | 500 | 08/06/2026, 13:18 | 1 | 247 | 247 | 244 | 431 | 426 | 427 | [12 empty] | 185 mm² |  | 13 | 18 | 43 | 31 | 185 mm² |  | 16 | 0 | 0 | 13 | [6 empty] | 240 mm² |  | 12 | 1 | 3 | 10 | [14 empty] | Total Load R: 41; Total Load Y: 19; Total Load B: 46; Total Load N: 54 | 46 | 19 | 6.8679 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.222932, 56.597011 | 904 | Pole (PMT) | 3 | 100 | 08/06/2026, 13:11 | 1 | 240 | 241 | 213 | 420 | 418 | 401 | 50 mm² |  | 13 | 14 | 4 | 8 | 50 mm² |  | 18 | 4 | 4 | 13 | [38 empty] | Total Load R: 31; Total Load Y: 18; Total Load B: 8; Total Load N: 21 | 31 | 8 | 22.5513 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.232023, 56.597079 | 903 | Pole (PMT) |  | 315 | 08/06/2026, 13:06 | 1 | 247 | 247 | 245 | 431 | 428 | 428 | 120 mm² |  | 16 | 22 | 20 | 19 | 120 mm² |  | 20 | 16 | 24 | 14 | [38 empty] | Total Load R: 36; Total Load Y: 38; Total Load B: 44; Total Load N: 33 | 44 | 36 | 10.4275 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.235702, 56.598578 | 2029 | Pole (PMT) |  | 315 | 08/06/2026, 13:02 | 1 | 247 | 248 | 245 | 432 | 428 | 430 | 185 mm² |  | 1 | 0 | 0 | 1 | [44 empty] | Total Load R: 1; Total Load Y: 0; Total Load B: 0; Total Load N: 1 | 1 | 0 | 0.23754 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.237867, 56.597585 | 902 | Pole (PMT) |  | 315 | 08/06/2026, 12:59 | 1 | 248 | 248 | 245 | 431 | 430 | 429 | 120 mm² |  | 3 | 1 | 0 | 3 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 3; Total Load Y: 1; Total Load B: 0; Total Load N: 3 | 3 | 0 | 0.71097 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN04 | 23.252933, 56.554429 | 1418 | Pole (PMT) |  | 315 | 05/06/2026, 13:32 | 1 | 239 | 238 | 240 | 414 | 415 | 415 | 185 mm² |  | 31 | 19 | 13 | 12 | 240 mm² |  | 90 | 120 | 55 | 49 | [38 empty] | Total Load R: 121; Total Load Y: 139; Total Load B: 68; Total Load N: 61 | 139 | 68 | 31.6421 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN04 | 23.247757, 56.555289 | 1532 | Pole (PMT) |  | 200 | 05/06/2026, 13:00 | 1 | 244 | 247 | 247 | 426 | 431 | 427 | 240 mm² |  | 120 | 101 | 78 | 36 | [44 empty] | Total Load R: 120; Total Load Y: 101; Total Load B: 78; Total Load N: 36 | 120 | 78 | 44.2712 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN04 | 23.241754, 56.565237 | 1846 | Pole (PMT) |  | 315 | 05/06/2026, 12:51 | 1 | 247 | 250 | 249 | 433 | 437 | 431 | 185 mm² |  | 15 | 0 | 3 | 11 | 185 mm² |  | 3 | 28 | 13 | 14 | [38 empty] | Total Load R: 18; Total Load Y: 28; Total Load B: 16; Total Load N: 25 | 28 | 16 | 6.6665 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN04 | 23.246315, 56.562587 | 265 | Pole (PMT) |  | 200 | 05/06/2026, 12:45 | 1 | 246 | 250 | 249 | 431 | 436 | 431 | 120 mm² |  | 50 | 23 | 23 | 18 | 185 mm² |  | 85 | 34 | 84 | 48 | [38 empty] | Total Load R: 135; Total Load Y: 57; Total Load B: 107; Total Load N: 66 | 135 | 57 | 50.3897 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN04 | 23.245269, 56.559067 | 266 | Pole (PMT) |  | 200 | 05/06/2026, 12:40 | 1 | 248 | 251 | 250 | 433 | 437 | 432 | 185 mm² |  | 52 | 36 | 63 | 20 | 185 mm² |  | 1 | 0 | 0 | 1 | [38 empty] | Total Load R: 53; Total Load Y: 36; Total Load B: 63; Total Load N: 21 | 63 | 36 | 23.6243 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN04 | 23.246541, 56.559388 | 1477 | Ground (GMT) |  | 1000 | 05/06/2026, 12:35 | 1 | 249 | 252 | 251 | 434 | 439 | 435 | [24 empty] | 185 mm² |  | 22 | 1 | 1 | 13 | 185 mm² |  | 1 | 0 | 0 | 1 | 185 mm² |  | 17 | 24 | 8 | 17 | 185 mm² |  | 23 | 24 | 18 | 8 |  |  | Total Load R: 63; Total Load Y: 49; Total Load B: 27; Total Load N: 39 | 63 | 27 | 4.7358 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN04 | 23.249898, 56.557093 | 2020 | Ground (GMT) |  | 1000 | 05/06/2026, 12:25 | 1 | 249 | 251 | 251 | 435 | 438 | 434 | [24 empty] | 240 mm² |  | 31 | 42 | 52 | 25 | 185 mm² |  | 27 | 73 | 2 | 56 | 185 mm² |  | 1 | 0 | 10 | 8 | 185 mm² |  | 45 | 40 | 76 | 34 |  |  | Total Load R: 104; Total Load Y: 155; Total Load B: 140; Total Load N: 123 | 155 | 104 | 11.6784 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN01 |  | 1533 | Pole (PMT) |  | 100 | 04/06/2026, 12:22 | 1 | 246 | 246 | 246 | 430 | 428 | 427 | 120 mm² |  | 15 | 5 | 7 | 6 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 15; Total Load Y: 5; Total Load B: 7; Total Load N: 6 | 15 | 5 | 11.1717 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN01 | 23.261301, 56.555112 | 1370 | Ground (GMT) |  | 1000 | 04/06/2026, 12:15 | 1 | 242 | 245 | 242 | 428 | 427 | 426 | [12 empty] | 120 mm² |  | 0 | 0 | 0 | 0 | 120 mm² |  | 60 | 61 | 65 | 4 | 120 mm² |  | 1 | 2 | 1 | 1 | 120 mm² |  | 45 | 48 | 50 | 3 | 120 mm² |  | 60 | 71 | 65 | 3 | 120 mm² |  | 65 | 78 | 45 | 3 |  |  | Total Load R: 231; Total Load Y: 260; Total Load B: 226; Total Load N: 14 | 260 | 226 | 19.2743 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN01 | 23.261296, 56.555117 | 263 | Ground (GMT) |  | 1000 | 04/06/2026, 12:16 | 1 | 246 | 248 | 247 | 428 | 426 | 427 | [6 empty] | 120 mm² |  | 28 | 26 | 25 | 0 | 120 mm² |  | 25 | 26 | 24 | 0 | 120 mm² |  | 15 | 20 | 18 | 0 | 120 mm² |  | 25 | 28 | 25 | 0 | 120 mm² |  | 15 | 14 | 13 | 0 | 120 mm² |  | 15 | 17 | 10 | 0 | 120 mm² |  | 15 | 17 | 20 | 0 |  |  | Total Load R: 138; Total Load Y: 148; Total Load B: 135; Total Load N: 0 | 148 | 135 | 10.9715 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN01 | 23.255158, 56.55263 | 261 | Ground (GMT) |  | 1000 | 04/06/2026, 12:01 | 1 | 246 | 248 | 247 | 430 | 429 | 433 | 120 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 110 | 101 | 75 | 60 | 185 mm² |  | 50 | 60 | 45 | 29 | 240 mm² |  | 110 | 99 | 60 | 50 | 185 mm² |  | 50 | 60 | 77 | 45 | 240 mm² |  | 90 | 91 | 81 | 35 | 240 mm² |  | 60 | 48 | 34 | 31 |  |  | Total Load R: 470; Total Load Y: 459; Total Load B: 372; Total Load N: 250 | 470 | 372 | 35.0047 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN01 | 23.258778, 56.553372 | 264 | Ground (GMT) |  | 1000 | 04/06/2026, 11:55 | 1 | 246 | 249 | 249 | 430 | 431 | 435 | [6 empty] | 185 mm² |  | 110 | 65 | 35 | 60 | 185 mm² |  | 65 | 35 | 15 | 20 | 240 mm² |  | 20 | 10 | 50 | 25 | 240 mm² |  | 33 | 65 | 88 | 30 | 185 mm² |  | 20 | 18 | 4 | 12 | 185 mm² |  | 95 | 54 | 60 | 29 | 185 mm² |  | 60 | 75 | 73 | 35 |  |  | Total Load R: 403; Total Load Y: 322; Total Load B: 325; Total Load N: 211 | 403 | 322 | 30.0147 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN01 | 23.261262, 56.554218 | 2285 | Ground (GMT) |  | 1000 | 04/06/2026, 11:48 | 1 | 247 | 250 | 249 | 422 | 436 | 436 | 185 mm² |  | 70 | 10 | 7 | 20 | 185 mm² |  | 45 | 50 | 40 | 6 | 185 mm² |  | 68 | 75 | 60 | 25 | 120 mm² |  | 30 | 18 | 28 | 20 | 185 mm² |  | 20 | 2 | 3 | 10 | [20 empty] | Total Load R: 233; Total Load Y: 155; Total Load B: 138; Total Load N: 81 | 233 | 138 | 17.0306 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN01 | 23.2586, 56.55988 | 4736 | Pole (PMT) |  | 100 | 04/06/2026, 11:43 | 1 | 246 | 241 | 247 | 443 | 438 | 439 | 185 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN01 | 23.255843, 56.552175 | 2348 | Ground (GMT) |  | 1000 | 04/06/2026, 11:41 | 1 | 248 | 251 | 250 | 432 | 441 | 432 | 185 mm² |  | 10 | 20 | 4 | 7 | [6 empty] | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 10; Total Load Y: 20; Total Load B: 4; Total Load N: 7 | 20 | 4 | 1.4965 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN01 | 23.255637, 56.561195 | 2385 | Ground (GMT) |  | 1000 | 04/06/2026, 11:37 | 1 | 248 | 251 | 250 | 443 | 438 | 441 | 185 mm² |  | 10 | 0 | 8 | 6 | [44 empty] | Total Load R: 10; Total Load Y: 0; Total Load B: 8; Total Load N: 6 | 10 | 0 | 0.7673 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN01 | 23.25607, 56.557604 | 262 | Ground (GMT) |  | 1000 | 04/06/2026, 11:33 | 1 | 247 | 249 | 248 | 432 | 430 | 435 | [6 empty] | 50 mm² |  | 20 | 1 | 0 | 20 | 120 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 2 | 17 | 16 | 8 | 240 mm² |  | 186 | 190 | 200 | 70 | 185 mm² |  | 70 | 85 | 66 | 36 | 185 mm² |  | 50 | 56 | 42 | 17 | 185 mm² |  | 70 | 60 | 35 | 30 |  |  | Total Load R: 398; Total Load Y: 409; Total Load B: 359; Total Load N: 181 | 409 | 359 | 30.6033 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN02 | 23.308062, 56.586227 | 4689 | Ground (GMT) |  | 1000 | 02/06/2026, 21:59 | 1 | 246 | 249 | 248 | 433 | 430 | 433 | 185 mm² |  | 288 | 193 | 182 | 214 | [44 empty] | Total Load R: 288; Total Load Y: 193; Total Load B: 182; Total Load N: 214 | 288 | 182 | 21.5994 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN02 | 23.308062, 56.586227 | 4689 | Ground (GMT) | 3 | 1000 | 07/06/2026, 08:57 | 2 | 246 | 249 | 248 | 431 | 436 | 431 | 300 mm² |  | 368 | 240 | 370 | 158 | [44 empty] | Total Load R: 368; Total Load Y: 240; Total Load B: 370; Total Load N: 158 | 370 | 240 | 27.621 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.238908, 56.606715 | 874 | Pole (PMT) |  | 315 | 01/06/2026, 14:30 | 1 | 246 | 244 | 243 | 427 | 426 | 422 | 185 mm² |  | 0 | 14 | 0 | 10 | 120 mm² |  | 50 | 51 | 20 | 32 | [38 empty] | Total Load R: 50; Total Load Y: 65; Total Load B: 20; Total Load N: 42 | 65 | 20 | 15.2613 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.241583, 56.606095 | 2114 | Pole (PMT) |  | 315 | 01/06/2026, 14:27 | 1 | 234 | 236 | 232 | 410 | 415 | 420 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 15 | 0 | 7 | 1 | [38 empty] | Total Load R: 15; Total Load Y: 0; Total Load B: 7; Total Load N: 1 | 15 | 0 | 3.3816 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.241812, 56.610512 | 2028 | Pole (PMT) |  | 315 | 01/06/2026, 14:24 | 1 | 245 | 247 | 243 | 430 | 425 | 427 | 185 mm² |  | 2 | 0 | 9 | 5 | 185 mm² |  | 2 | 10 | 11 | 5 | [38 empty] | Total Load R: 4; Total Load Y: 10; Total Load B: 20; Total Load N: 10 | 20 | 4 | 4.7288 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.242138, 56.623042 | 4382 | Pole (PMT) |  | 100 | 01/06/2026, 14:21 | 1 | 245 | 247 | 244 | 430 | 424 | 427 | 185 mm² |  | 1 | 0 | 0 | 1 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 1; Total Load Y: 0; Total Load B: 0; Total Load N: 1 | 1 | 0 | 0.74478 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.242734, 56.636093 | 04490 | Pole (PMT) |  | 100 | 01/06/2026, 14:18 | 1 | 244 | 246 | 245 | 428 | 425 | 424 | 185 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.243012, 56.629505 | 2261 | Ground (GMT) |  | 1000 | 01/06/2026, 14:14 | 1 | 241 | 242 | 243 | 422 | 424 | 420 | 185 mm² |  | 2 | 30 | 15 | 18 | 185 mm² |  | 0 | 0 | 0 | 0 | 240 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 2; Total Load Y: 30; Total Load B: 15; Total Load N: 18 | 30 | 2 | 2.1928 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.240065, 56.627353 | 2260 | Ground (GMT) |  | 1000 | 01/06/2026, 14:10 | 1 | 242 | 243 | 242 | 422 | 424 | 420 | 185 mm² |  | 15 | 11 | 0 | 10 | [44 empty] | Total Load R: 15; Total Load Y: 11; Total Load B: 0; Total Load N: 10 | 15 | 0 | 1.0964 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.238313, 56.625593 | 03703 | Ground (GMT) |  | 500 | 01/06/2026, 14:07 | 1 | 241 | 243 | 240 | 421 | 421 | 423 | 240 mm² |  | 11 | 0 | 0 | 7 | [44 empty] | Total Load R: 11; Total Load Y: 0; Total Load B: 0; Total Load N: 7 | 11 | 0 | 1.6042 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.237045, 56.6227 | 1758 | Pole (PMT) |  | 100 | 01/06/2026, 14:04 | 1 | 242 | 243 | 240 | 424 | 427 | 422 | 120 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.244752, 56.61361 | 875 | Pole (PMT) |  | 100 | 01/06/2026, 14:00 | 1 | 242 | 243 | 240 | 425 | 423 | 421 | 120 mm² |  | 0 | 0 | 1 | 1 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 1; Total Load N: 1 | 1 | 0 | 0.73612 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.247957, 56.616398 | 4495 | Pole (PMT) |  | 200 | 01/06/2026, 13:56 | 1 | 242 | 244 | 240 | 425 | 419 | 420 | 185 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.250042, 56.619795 | 901 | Pole (PMT) |  | 315 | 01/06/2026, 13:53 | 1 | 240 | 241 | 239 | 419 | 415 | 417 | 185 mm² |  | 6 | 15 | 0 | 9 | 120 mm² |  | 135 | 75 | 71 | 49 | [38 empty] | Total Load R: 141; Total Load Y: 90; Total Load B: 71; Total Load N: 58 | 141 | 71 | 32.485 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.245717, 56.607107 | 873 | Pole (PMT) |  | 315 | 01/06/2026, 13:49 | 1 | 241 | 242 | 243 | 421 | 425 | 420 | 120 mm² |  | 22 | 17 | 39 | 15 | 120 mm² |  | 1 | 15 | 39 | 21 | [38 empty] | Total Load R: 23; Total Load Y: 32; Total Load B: 78; Total Load N: 36 | 78 | 23 | 18.0562 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.252338, 56.608297 | 2128 | Pole (PMT) |  | 315 | 01/06/2026, 13:46 | 1 | 242 | 243 | 241 | 422 | 419 | 420 | 185 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.24736, 56.602865 | 2048 | Pole (PMT) |  | 315 | 01/06/2026, 13:43 | 1 | 242 | 243 | 240 | 424 | 425 | 422 | 185 mm² |  | 9 | 11 | 15 | 7 | [44 empty] | Total Load R: 9; Total Load Y: 11; Total Load B: 15; Total Load N: 7 | 15 | 9 | 3.4971 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.246575, 56.599925 | 872 | Pole (PMT) |  | 315 | 01/06/2026, 13:41 | 1 | 241 | 240 | 242 | 422 | 424 | 421 | 120 mm² |  | 31 | 25 | 39 | 15 | 120 mm² |  | 90 | 101 | 15 | 20 | [38 empty] | Total Load R: 121; Total Load Y: 126; Total Load B: 54; Total Load N: 35 | 126 | 54 | 29.237 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.243841, 56.595035 | 2192 | Ground (GMT) |  | 1000 | 01/06/2026, 13:38 | 1 | 243 | 244 | 241 | 426 | 420 | 427 | 185 mm² |  | 60 | 25 | 35 | 31 | 185 mm² |  | 81 | 75 | 79 | 25 | [38 empty] | Total Load R: 141; Total Load Y: 100; Total Load B: 114; Total Load N: 56 | 141 | 100 | 10.4037 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.242493, 56.59283 | 871 | Pole (PMT) |  | 315 | 01/06/2026, 13:35 | 1 | 245 | 246 | 244 | 424 | 425 | 423 | 120 mm² |  | 50 | 40 | 90 | 45 | 120 mm² |  | 3 | 1 | 5 | 3 | [38 empty] | Total Load R: 53; Total Load Y: 41; Total Load B: 95; Total Load N: 48 | 95 | 41 | 22.1483 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.245258, 56.589365 | 2179 | Pole (PMT) |  | 315 | 01/06/2026, 13:32 | 1 | 245 | 244 | 246 | 425 | 424 | 423 | 240 mm² |  | 40 | 25 | 40 | 25 | 185 mm² |  | 45 | 11 | 60 | 40 | [38 empty] | Total Load R: 85; Total Load Y: 36; Total Load B: 100; Total Load N: 65 | 100 | 36 | 23.3689 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.247745, 56.590335 | 870 | Pole (PMT) |  | 315 | 01/06/2026, 13:29 | 1 | 245 | 245 | 243 | 427 | 425 | 426 | 120 mm² |  | 7 | 22 | 25 | 15 | 120 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 7; Total Load Y: 22; Total Load B: 25; Total Load N: 15 | 25 | 7 | 5.8697 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.2499, 56.579493 | 1929 | Pole (PMT) |  | 315 | 01/06/2026, 13:27 | 1 | 246 | 245 | 244 | 431 | 429 | 420 | 185 mm² |  | 0 | 0 | 0 | 0 | [44 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.249742, 56.57583 | 869 | Pole (PMT) |  | 315 | 01/06/2026, 13:25 | 1 | 245 | 247 | 248 | 428 | 420 | 431 | 185 mm² |  | 40 | 39 | 67 | 30 | 185 mm² |  | 90 | 25 | 15 | 57 | [38 empty] | Total Load R: 130; Total Load Y: 64; Total Load B: 82; Total Load N: 87 | 130 | 64 | 30.5941 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.252418, 56.570365 | 1662 | Pole (PMT) |  | 315 | 01/06/2026, 13:22 | 1 | 247 | 245 | 247 | 432 | 431 | 430 | 185 mm² |  | 20 | 8 | 0 | 5 | 185 mm² |  | 25 | 15 | 19 | 7 | [38 empty] | Total Load R: 45; Total Load Y: 23; Total Load B: 19; Total Load N: 12 | 45 | 19 | 10.6892 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.247045, 56.570727 | 2099 | Pole (PMT) |  | 315 | 01/06/2026, 13:18 | 1 | 248 | 247 | 245 | 432 | 431 | 429 | 185 mm² |  | 0 | 0 | 0 | 0 | 185 mm² |  | 2 | 15 | 1 | 9 | [38 empty] | Total Load R: 2; Total Load Y: 15; Total Load B: 1; Total Load N: 9 | 15 | 1 | 3.5631 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.249442, 56.56817 | 1843 | Pole (PMT) |  | 315 | 01/06/2026, 13:15 | 1 | 246 | 247 | 248 | 431 | 430 | 429 | 185 mm² |  | 20 | 30 | 69 | 40 | 120 mm² |  | 64 | 50 | 75 | 30 | [38 empty] | Total Load R: 84; Total Load Y: 80; Total Load B: 144; Total Load N: 70 | 144 | 80 | 34.1263 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.249553, 56.564793 | 1527 | Pole (PMT) |  | 315 | 01/06/2026, 13:12 | 1 | 248 | 248 | 246 | 432 | 427 | 428 |  |  | 25 | 45 | 31 | 30 | 240 mm² |  | 40 | 15 | 31 | 18 | 185 mm² |  | 0 | 0 | 0 | 0 | [32 empty] | Total Load R: 65; Total Load Y: 60; Total Load B: 62; Total Load N: 48 | 65 | 60 | 15.44 | OK - No Upgrade | OK - Balanced
Araqi | AL TAYYEB INDUSTRIAL | K_LN05 | 23.251998, 56.55637 | 2315 | Pole (PMT) |  | 315 | 01/06/2026, 13:09 | 1 | 249 | 248 | 247 | 435 | 431 | 430 | 185 mm² |  | 1 | 21 | 1 | 16 | [44 empty] | Total Load R: 1; Total Load Y: 21; Total Load B: 1; Total Load N: 16 | 21 | 1 | 5.0229 | OK - No Upgrade | Need to Balance
Araqi | AL TAYYEB INDUSTRIAL | K_LN03 | 23.28049, 56.552073 | 415 | Ground (GMT) |  | 1000 | 01/06/2026, 09:17 | 1 | 244 | 243 | 245 | 422 | 425 | 425 | [18 empty] | 185 mm² |  | 88 | 76 | 65 | 37 | 185 mm² |  | 95 | 88 | 97 | 31 | 185 mm² |  | 147 | 100 | 115 | 57 | 185 mm² |  | 75 | 35 | 135 | 80 | 185 mm² |  | 49 | 108 | 135 | 85 |  |  | Total Load R: 454; Total Load Y: 407; Total Load B: 547; Total Load N: 290 | 547 | 407 | 39.9816 | OK - No Upgrade | Need to Balance

## AL BANAH
Team Name | Primary Substation | H.T Feeder No. | Location | Tx. No. | Type | Tap No. | Capacity | Time & Date | Reading No. | Voltage Value | [5 empty] | Feeder 1 | [5 empty] | Feeder 2 | [5 empty] | Feeder 3 | [5 empty] | Feeder 4 | [5 empty] | Feeder 5 | [5 empty] | Feeder 6 | [5 empty] | Feeder 7 | [5 empty] | Feeder 8 | [5 empty] | Total Load |  |  |  | MAX Value | MIN Value | Load % | Action (Upgrade) | Action (Balance)
[10 empty] | Phase Voltage |  |  | Line Voltage |  |  | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | Cable mm² | Type | R | Y | B | N | R | Y | B | N
[10 empty] | R/N | Y/N | B/N | R/Y | R/B | Y/B
Araqi | AL BANAH | K_LN03 | 23.318543, 57.028923 | 1470 | Pole (PMT) |  | 100 | 13/06/2026, 13:59 | 1 | 220 | 221 | 222 | 381 | 384 | 384 | 185 mm² |  | 32 | 4 | 3 | 25 | [38 empty] | Total Load R: 32; Total Load Y: 4; Total Load B: 3; Total Load N: 25 | 32 | 3 | 21.1172 | OK - No Upgrade | Need to Balance
Araqi | AL BANAH | K_LN03 | 23.3146, 56.598179 | 1467 | Ground (GMT) |  | 1000 | 13/06/2026, 13:50 | 1 | 231 | 234 | 233 | 401 | 408 | 402 | [12 empty] | 185 mm² |  | 20 | 21 | 45 | 23 | 185 mm² |  | 21 | 11 | 20 | 9 | 120 mm² |  | 0 | 0 | 0 | 0 | [14 empty] | 68 | 174 | 147 | 94 | 109 | 206 | 212 | 126 | 212 | 109 | 14.7245 | OK - No Upgrade | Need to Balance
Araqi | AL BANAH | K_LN03 | 23.328332, 57.026825 | 2262 | Pole (PMT) |  | 200 | 13/06/2026, 13:42 | 1 | 232 | 235 | 236 | 407 | 408 | 403 | 185 mm² |  | 12 | 0 | 0 | 8 | 120 mm² |  | 11 | 0 | 0 | 8 | [32 empty] | Total Load R: 23; Total Load Y: 0; Total Load B: 0; Total Load N: 16 | 23 | 0 | 8.1069 | OK - No Upgrade | Need to Balance
Araqi | AL BANAH | K_LN03 | 23.331083, 57.026075 | 4684 | Pole (PMT) | 3 | 100 | 13/06/2026, 13:31 | 1 | 234 | 236 | 233 | 410 | 409 | 405 | 185 mm² |  | 0 | 0 | 0 | 0 | [38 empty] | Total Load R: 0; Total Load Y: 0; Total Load B: 0; Total Load N: 0 | 0 | 0 | 0 | OK - No Upgrade | OK - Balanced
Araqi | AL BANAH | K_LN03 | 23.333427, 57.025223 | 4662 | Pole (PMT) |  | 315 | 13/06/2026, 13:19 | 1 | 235 | 236 | 234 | 410 | 418 | 405 | 185 mm² |  | 79 | 124 | 59 | 50 | 185 mm² |  | 17 | 13 | 6 | 9 | [32 empty] | Total Load R: 96; Total Load Y: 137; Total Load B: 65; Total Load N: 59 | 137 | 65 | 30.8855 | OK - No Upgrade | Need to Balance
Araqi | AL BANAH | K_LN03 | 23.336407, 57.025112 | 1266 | Pole (PMT) |  | 315 | 13/06/2026, 13:10 | 1 | 238 | 235 | 236 | 414 | 410 | 413 | 185 mm² |  | 4 | 29 | 16 | 21 | 185 mm² |  | 8 | 20 | 10 | 6 | [32 empty] | Total Load R: 12; Total Load Y: 49; Total Load B: 26; Total Load N: 27 | 49 | 12 | 11.1544 | OK - No Upgrade | Need to Balance
Araqi | AL BANAH | K_LN03 | 23.338354, 57.026037 | 2064 | Pole (PMT) |  | 100 | 13/06/2026, 12:58 | 1 | 238 | 241 | 236 | 419 | 416 | 412 | 120 mm² |  | 18 | 2 | 21 | 13 | [38 empty] | Total Load R: 18; Total Load Y: 2; Total Load B: 21; Total Load N: 13 | 21 | 2 | 15.2403 | OK - No Upgrade | Need to Balance
Araqi | AL BANAH | K_LN03 | 23.339375, 57.028256 | 1265 | Pole (PMT) |  | 100 | 13/06/2026, 12:53 | 1 | 236 | 239 | 239 | 411 | 417 | 413 | 185 mm² |  | 12 | 2 | 10 | 9 | 120 mm² |  | 25 | 9 | 27 | 19 | [32 empty] | Total Load R: 37; Total Load Y: 11; Total Load B: 37; Total Load N: 28 | 37 | 11 | 26.3393 | OK - No Upgrade | Need to Balance
Araqi | AL BANAH | K_LN03 | 23.345079, 57.02799 | 1264 | Pole (PMT) |  | 100 | 13/06/2026, 12:45 | 1 | 234 | 233 | 239 | 406 | 410 | 412 | 120 mm² |  | 10 | 9 | 0 | 10 | 120 mm² |  | 64 | 80 | 24 | 36 | [32 empty] | Total Load R: 74; Total Load Y: 89; Total Load B: 24; Total Load N: 46 | 89 | 24 | 62.5859 | OK - No Upgrade | Need to Balance
Araqi | AL BANAH | K_LN03 | 23.276162, 56.965206 | 2124 | Pole (PMT) | 3 | 315 | 13/06/2026, 12:22 | 1 | 243 | 243 | 246 | 422 | 426 | 425 | 185 mm² |  | 36 | 48 | 32 | 17 | [38 empty] | Total Load R: 36; Total Load Y: 48; Total Load B: 32; Total Load N: 17 | 48 | 32 | 11.1379 | OK - No Upgrade | Need to Balance
Araqi | AL BANAH | K_LN03 | 23.281428, 56.975116 | 672 | Pole (PMT) |  | 315 | 13/06/2026, 12:12 | 1 | 243 | 243 | 246 | 420 | 425 | 426 | 120 mm² |  | 29 | 2 | 10 | 19 | 185 mm² |  | 61 | 87 | 47 | 28 | [32 empty] | Total Load R: 90; Total Load Y: 89; Total Load B: 57; Total Load N: 47 | 90 | 57 | 20.7846 | OK - No Upgrade | Need to Balance
Araqi | AL BANAH | K_LN03 | 23.279521, 56.970611 | 2076 | Pole (PMT) |  | 100 | 13/06/2026, 12:00 | 1 | 232 | 233 | 235 | 402 | 407 | 407 | 50 mm² |  | 10 | 6 | 3 | 6 | [38 empty] | Total Load R: 10; Total Load Y: 6; Total Load B: 3; Total Load N: 6 | 10 | 3 | 6.9628 | OK - No Upgrade | Need to Balance
Araqi | AL BANAH | K_LN03 |  | 666 | Ground (GMT) |  | 500 | 02/06/2026, 22:05 | 1 | 239 | 238 | 239 | 415 | 416 | 417 | 185 mm² |  | 89 | 101 | 156 | 44 | 185 mm² |  | 101 | 165 | 199 | 46 | [32 empty] | Total Load R: 190; Total Load Y: 266; Total Load B: 355; Total Load N: 90 | 355 | 190 | 51.0349 | OK - No Upgrade | Need to Balance
Araqi | AL BANAH | K_LN03 |  | 667 | Ground (GMT) |  | 500 | 02/06/2026, 22:04 | 1 | 238 | 239 | 238 | 414 | 416 | 415 | 185 mm² |  | 16 | 130 | 117 | 46 |  |  | 11 | 140 | 146 | 51 | [32 empty] | Total Load R: 27; Total Load Y: 270; Total Load B: 263; Total Load N: 97 | 270 | 27 | 38.7217 | OK - No Upgrade | Need to Balance
Araqi | AL BANAH | K_LN02 | 23.308061, 56.58623 | 652 | Ground (GMT) |  | 500 | 02/06/2026, 22:03 | 1 | 239 | 240 | 238 | 416 | 417 | 414 | 185 mm² |  | 156 | 149 | 109 | 60 | 185 mm² |  | 51 | 109 | 109 | 25 | [32 empty] | Total Load R: 207; Total Load Y: 258; Total Load B: 218; Total Load N: 85 | 258 | 207 | 37.1795 | OK - No Upgrade | Need to Balance